## Sheet1
code | faultName | message | severity | cause | explanation | recommendedAction | callhome | autoCleared | type | moClass | affectedMoDn | mibFaultCode | mibFaultName
F0156 | fltFabricComputeSlotEpMisplacedInChassisSlot | Server, vendor([vendor]), model([model]), serial([serial]) in slot [chassisId]/[slotId] presence: [presence] | warning | server-moved | This fault typically occurs when Cisco UCS Manager detects a server in a chassis slot that does not match what was previously equipped in the slot. | If you see this fault, take the following actions: - If the previous server was intentionally removed and a new one was inserted, reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | fabric:ComputeSlotEp | fabric/server/chassis-[chassisId]/slot-[slotId] | 156 | fltFabricComputeSlotEpMisplacedInChassisSlot
F0157 | fltFabricComputeSlotEpServerIdentificationProblem | Problem identifying server in slot [chassisId]/[slotId] | warning | server-identification-problem | This fault typically occurs when Cisco UCS Manager encountered a problem identifying the server in a chassis slot. | If you see this fault, take the following actions: - Remove and reinsert the server. - Reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | fabric:ComputeSlotEp | fabric/server/chassis-[chassisId]/slot-[slotId] | 157 | fltFabricComputeSlotEpServerIdentificationProblem
F0169 | fltVnicEtherConfig-failed | Eth vNIC [name], service profile [name] failed to apply configuration | minor | configuration-failed | This fault typically occurs when Cisco UCS Manager could not place the vNIC on the vCon. | If you see this fault, take the following actions: - Verify that the server was successfully discovered. - Verify that the correct type of adapters are installed on the server. - Confirm that the vCon assignment is correct. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | configuration | vnic:Ether | org-[name]/tier-[name]/ls-[name]/ether-[name] | 169 | fltVnicEtherConfigFailed
F0170 | fltVnicFcConfig-failed | FC vHBA [name], service profile [name] failed to apply configuration | minor | configuration-failed | This fault typically occurs when Cisco UCS Manager could not place the vHBA on the vCon. | If you see this fault, take the following actions: - Verify that the server was successfully discovered. - Verify that the correct type of adapters are installed on the server. - Confirm that the vCon assignment is correct. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | configuration | vnic:Fc | org-[name]/tier-[name]/ls-[name]/fc-[name] | 170 | fltVnicFcConfigFailed
F0174 | fltProcessorUnitInoperable | Processor [id] on server [chassisId]/[slotId] operability: [operability] | major | equipment-inoperable | This fault occurs in the unlikely event that processor is inoperable. | If you see this fault, take the following actions: - If the fault occurs on a blade server processor, remove the server from the chassis and then reinsert it. - In Cisco UCS Manager, decommission and then recommission the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | processor:Unit | sys/chassis-[id]/blade-[slotId]/board/cpu-[id] | 174 | fltProcessorUnitInoperable
F0175 | fltProcessorUnitThermalNonCritical | Processor [id] on server [chassisId]/[slotId] temperature: [thermal]Processor [id] on server [id] temperature: [thermal] | minor | thermal-problem | This fault occurs when the processor temperature on a blade or rack server exceeds a non-critical threshold value, but is still below the critical threshold. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the server. - Review the Cisco UCS Site Preparation Guide to ensure the servers have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis or rack server are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | processor:Unit | sys/chassis-[id]/blade-[slotId]/board/cpu-[id] | 175 | fltProcessorUnitThermalNonCritical
F0176 | fltProcessorUnitThermalThresholdCritical | Processor [id] on server [chassisId]/[slotId] temperature: [thermal]Processor [id] on server [id] temperature: [thermal] | major | thermal-problem | This fault occurs when the processor temperature on a blade or rack server exceeds a critical threshold value. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the server. - Review the Cisco UCS Site Preparation Guide to ensure the servers have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis or rack server are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | processor:Unit | sys/chassis-[id]/blade-[slotId]/board/cpu-[id] | 176 | fltProcessorUnitThermalThresholdCritical
F0177 | fltProcessorUnitThermalThresholdNonRecoverable | Processor [id] on server [chassisId]/[slotId] temperature: [thermal]Processor [id] on server [id] temperature: [thermal] | critical | thermal-problem | This fault occurs when the processor temperature on a blade or rack server has been out of the operating range, and the issue is not recoverable. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the server. - Review the Cisco UCS Site Preparation Guide to ensure the servers have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis or rack server are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | processor:Unit | sys/chassis-[id]/blade-[slotId]/board/cpu-[id] | 177 | fltProcessorUnitThermalThresholdNonRecoverable
F0178 | fltProcessorUnitVoltageThresholdNonCritical | Processor [id] on server [chassisId]/[slotId] voltage: [voltage] | minor | voltage-problem | This fault occurs when the processor voltage is out of normal operating range, but hasn't yet reached a critical stage. Normally the processor recovers itself from this situation | If you see this fault, take the following actions: - Monitor the processor for further degradation. - If the fault occurs on a blade server processor, remove the server from the chassis and then reinsert it. - In Cisco UCS Manager, decommission and then recommission the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | processor:Unit | sys/chassis-[id]/blade-[slotId]/board/cpu-[id] | 178 | fltProcessorUnitVoltageThresholdNonCritical
F0179 | fltProcessorUnitVoltageThresholdCritical | Processor [id] on server [chassisId]/[slotId] voltage: [voltage] | major | voltage-problem | This fault occurs when the processor voltage has exceeded the specified hardware voltage rating. | If you see this fault, take the following actions: - If the fault occurs on a blade server processor, remove the server from the chassis and then reinsert it. - In Cisco UCS Manager, decommission and then recommission the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | processor:Unit | sys/chassis-[id]/blade-[slotId]/board/cpu-[id] | 179 | fltProcessorUnitVoltageThresholdCritical
F0180 | fltProcessorUnitVoltageThresholdNonRecoverable | Processor [id] on server [chassisId]/[slotId] voltage: [voltage] | critical | voltage-problem | This fault occurs when the processor voltage has exceeded the specified hardware voltage rating and may cause processor hardware damage or jeopardy. | If you see this fault, take the following actions: - If the fault occurs on a blade server processor, remove the server from the chassis and then reinsert it. - In Cisco UCS Manager, decommission and then recommission the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | processor:Unit | sys/chassis-[id]/blade-[slotId]/board/cpu-[id] | 180 | fltProcessorUnitVoltageThresholdNonRecoverable
F0181 | fltStorageLocalDiskInoperable | Local disk [id] on server [chassisId]/[slotId] operability: [operability]Local disk [id] on server [id] operability: [operability] | major | equipment-inoperable | This fault occurs when the local disk has become inoperable. | If you see this fault, take the following actions: - Insert the disk in a supported slot. - Remove and reinsert the local disk. - Replace the disk, if an additional disk is available. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | storage:LocalDisk | sys/chassis-[id]/blade-[slotId]/board/storage-[type]-[id]/disk-[id] | 181 | fltStorageLocalDiskInoperable
F0182 | fltStorageItemCapacityExceeded | Disk usage for partition [name] on fabric interconnect [id] exceeded 70% | minor | capacity-exceeded | This fault occurs when the partition disk usage exceeds 70% but is less than 90%. | If you see this fault, take the following actions: - Reduce the partition disk usage to less than 70% by deleting unused and unnecessary files. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | storage:Item | sys/switch-[id]/stor-part-[name] | 182 | fltStorageItemCapacityExceeded
F0183 | fltStorageItemCapacityWarning | Disk usage for partition [name] on fabric interconnect [id] exceeded 90% | major | capacity-exceeded | This fault occurs when the partition disk usage exceeds 90%. | If you see this fault, take the following actions: - Reduce the partition disk usage to less than 90% by deleting unused and unnecessary files. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | storage:Item | sys/switch-[id]/stor-part-[name] | 183 | fltStorageItemCapacityWarning
F0184 | fltMemoryUnitDegraded | DIMM [location] on server [chassisId]/[slotId] operability: [operability]DIMM [location] on server [id] operability: [operability] | minor | equipment-degraded | This fault occurs when a DIMM is in a degraded operability state. This state typically occurs when an excessive number of correctable ECC errors are reported on the DIMM by the server BIOS. | If you see this fault, take the following actions: - Monitor the error statistics on the degraded DIMM through Cisco UCS Manager. If the high number of errors persists, there is a high possibility of the DIMM becoming inoperable. - If the DIMM becomes inoperable, replace the DIMM. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | memory:Unit | sys/chassis-[id]/blade-[slotId]/board/memarray-[id]/mem-[id] | 184 | fltMemoryUnitDegraded
F0185 | fltMemoryUnitInoperable | DIMM [location] on server [chassisId]/[slotId] operability: [operability]DIMM [location] on server [id] operability: [operability] | major | equipment-inoperable | This fault typically occurs because an above threshold number of correctable or uncorrectable errors has occurred on a DIMM. The DIMM may be inoperable. | If you see this fault, take the following actions: - If the SEL is enabled, review the SEL statistics on the DIMM to determine which threshold was crossed. - If necessary, replace the DIMM. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | memory:Unit | sys/chassis-[id]/blade-[slotId]/board/memarray-[id]/mem-[id] | 185 | fltMemoryUnitInoperable
F0186 | fltMemoryUnitThermalThresholdNonCritical | DIMM [location] on server [chassisId]/[slotId] temperature: [thermal]DIMM [location] on server [id] temperature: [thermal] | minor | thermal-problem | This fault occurs when the temperature of a memory unit on a blade or rack server exceeds a non-critical threshold value, but is still below the critical threshold. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the server. - Review the Cisco UCS Site Preparation Guide to ensure the servers have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis or rack server are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | memory:Unit | sys/chassis-[id]/blade-[slotId]/board/memarray-[id]/mem-[id] | 186 | fltMemoryUnitThermalThresholdNonCritical
F0187 | fltMemoryUnitThermalThresholdCritical | DIMM [location] on server [chassisId]/[slotId] temperature: [thermal]DIMM [location] on server [id] temperature: [thermal] | major | thermal-problem | This fault occurs when the temperature of a memory unit on a blade or rack server exceeds a critical threshold value. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the server. - Review the Cisco UCS Site Preparation Guide to ensure the servers have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis or rack server are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | memory:Unit | sys/chassis-[id]/blade-[slotId]/board/memarray-[id]/mem-[id] | 187 | fltMemoryUnitThermalThresholdCritical
F0188 | fltMemoryUnitThermalThresholdNonRecoverable | DIMM [location] on server [chassisId]/[slotId] temperature: [thermal]DIMM [location] on server [id] temperature: [thermal] | critical | thermal-problem | This fault occurs when the temperature of a memory unit on a blade or rack server has been out of the operating range, and the issue is not recoverable.Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the server. - Review the Cisco UCS Site Preparation Guide to ensure the servers have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis or rack server are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | memory:Unit | sys/chassis-[id]/blade-[slotId]/board/memarray-[id]/mem-[id] | 188 | fltMemoryUnitThermalThresholdNonRecoverable
F0189 | fltMemoryArrayVoltageThresholdNonCritical | Memory array [id] on server [chassisId]/[slotId] voltage: [voltage]Memory array [id] on server [id] voltage: [voltage] | minor | voltage-problem | This fault occurs when the memory array voltage is out of normal operating range, but hasn't yet reached a critical stage. Typically the memory array recovers itself from this situation. | If you see this fault, take the following actions: - If the SEL is enabled, look at the SEL statistics on the DIMM to determine which threshold was crossed. - Monitor the memory array for further degradation. - If the fault occurs on a blade server memory array, remove the blade and re-insert into the chassis. - In Cisco UCS Manager, decommission and recommission the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | memory:Array | sys/chassis-[id]/blade-[slotId]/board/memarray-[id] | 189 | fltMemoryArrayVoltageThresholdNonCritical
F0190 | fltMemoryArrayVoltageThresholdCritical | Memory array [id] on server [chassisId]/[slotId] voltage: [voltage]Memory array [id] on server [id] voltage: [voltage] | major | voltage-problem | This fault occurs when the memory array voltage exceeds the specified hardware voltage rating | If you see this fault, take the following actions: - If the SEL is enabled, look at the SEL statistics on the DIMM to determine which threshold was crossed. - Monitor the memory array for further degradation. - If the fault occurs on a blade server memory array, remove the blade and re-insert into the chassis. - In Cisco UCS Manager, decommission and recommission the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | memory:Array | sys/chassis-[id]/blade-[slotId]/board/memarray-[id] | 190 | fltMemoryArrayVoltageThresholdCritical
F0191 | fltMemoryArrayVoltageThresholdNonRecoverable | Memory array [id] on server [chassisId]/[slotId] voltage: [voltage]Memory array [id] on server [id] voltage: [voltage] | critical | voltage-problem | This fault occurs when the memory array voltage exceeded the specified hardware voltage rating and potentially memory hardware may be in damage or jeopardy | If you see this fault, take the following actions: - If the SEL is enabled, review the SEL statistics on the DIMM to determine which threshold was crossed. - Monitor the memory array for further degradation. - If the fault occurs on a blade server memory array, remove the server from the chassis and re-insert it. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | memory:Array | sys/chassis-[id]/blade-[slotId]/board/memarray-[id] | 191 | fltMemoryArrayVoltageThresholdNonRecoverable
F0200 | fltAdaptorUnitUnidentifiable-fru | Adapter [id] in server [id] has unidentified FRUAdapter [id] in server [chassisId]/[slotId] has unidentified FRU | major | unidentifiable-fru | This fault typically occurs because Cisco UCS Manager has detected an unsupported adapter. For example, the model, vendor, or revision is not recognized. | If you see this fault, take the following actions: - Verify that a supported adapter is installed. - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | adaptor:Unit | sys/chassis-[id]/blade-[slotId]/adaptor-[id] | 200 | fltAdaptorUnitUnidentifiableFru
F0203 | fltAdaptorUnitMissing | Adapter [id] in server [id] presence: [presence]Adapter [id] in server [chassisId]/[slotId] presence: [presence] | warning | equipment-missing | The adaptor is missing. Cisco UCS Manager raises this fault when any of the following scenarios occur: - The endpoint reports there is no adapter in the adaptor slot. - The endpoint cannot detect or communicate with the adapter in the adaptor slot. | If you see this fault, take the following actions: - Make sure an adapter is inserted in the adaptor slot in the server. - Check whether the adaptor is connected and configured properly and is running the recommended firmware version. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | adaptor:Unit | sys/chassis-[id]/blade-[slotId]/adaptor-[id] | 203 | fltAdaptorUnitMissing
F0206 | fltAdaptorUnitAdaptorReachability | Adapter [id]/[id] is unreachableAdapter [chassisId]/[slotId]/[id] is unreachable | info | connectivity-problem | Cisco UCS Manager cannot access the adapter. This fault typically occurs as a result of one of the following issues: - The server does not have sufficient power. - The I/O module is not functional. - The adapter firmware has failed. - The adapter is not functional | If you see this fault, take the following actions: - Check the POST results for the server. In Cisco UCS Manager GUI, you can access the POST results from the General tab for the server. In Cisco UCS Manager CLI, you can access the POST results through the show post command under the scope for the server. - In Cisco UCS Manager, check the power state of the server. - Verify that the physical server has the same power state. - If the server is off, turn the server on. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | connectivity | adaptor:Unit | sys/chassis-[id]/blade-[slotId]/adaptor-[id] | 206 | fltAdaptorUnitAdaptorReachability
F0207 | fltAdaptorHostIfLink-down | Adapter [transport] host interface [id]/[id]/[id] link state: [linkState]Adapter [transport] host interface [chassisId]/[slotId]/[id]/[id] link state: [linkState] | major | link-down | This fault typically occurs as a result of one of the following issues: - The fabric interconnect is in End-Host mode, and all uplink ports failed. - The server port to which the adapter is pinned failed. - A transient error caused the link to fail. | If you see this fault, take the following actions: - If an associated port is disabled, enable the port. - Reacknowledge the server with the adapter that has the failed link. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | adaptor:HostIf |  | 207 | fltAdaptorHostIfLinkDown
F0209 | fltAdaptorExtIfLink-down | Adapter uplink interface [id]/[id]/[id] link state: [linkState]Adapter uplink interface [chassisId]/[slotId]/[id]/[id] link state: [linkState] | major | link-down | The link for a network facing adapter interface is down. Cisco UCS Manager raises this fault when any of the following scenarios occur: - Cisco UCS Manager cannot establish and/or validate the adapter's connectivity to any of the fabric interconnects. - The endpoint reports a link down or vNIC down event on the adapter link. - The endpoint reports an errored link state or errored vNIC state event on the adapter link. | If you see this fault, take the following actions: - Verify that the adapter is connected, configured properly, and is running the recommended firmware version. - If the server is stuck at discovery, decommission the server and reacknowledge the server slot. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | adaptor:ExtIf |  | 209 | fltAdaptorExtIfLinkDown
F0276 | fltPortPIoLink-down | [transport] port [portId] on chassis [id] oper state: [operState], reason: [stateQual][transport] port [portId] on fabric interconnect [id] oper state: [operState], reason: [stateQual] | major | link-down | This fault occurs when a fabric interconnect port is in link-down state. This state impacts the traffic destined for the port. | If you see this fault, take the following actions: - Verify that the physical link is properly connected between the fabric interconnect and the peer component. - Verify that the configuration on the peer entity is properly configured and matches the fabric interconnect port configuration. - Unconfigure and re-configure the port. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | network | port:PIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 276 | fltPortPIoLinkDown
F0277 | fltPortPIoFailed | [transport] port [portId] on chassis [id] oper state: [operState], reason: [stateQual][transport] port [portId] on fabric interconnect [id] oper state: [operState], reason: [stateQual] | major | port-failed | This fault is raised on fabric interconnect ports and on server-facing ports on an IOM or a FEX module when the system detects an indeterminate fault. | If you see this fault, create a show tech-support file for Cisco UCS Manager and the chassis or FEX module, and then contact Cisco TAC. | diagnostic | TRUE | network | port:PIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 277 | fltPortPIoFailed
F0278 | fltPortPIoHardware-failure | [transport] port [portId] on chassis [id] oper state: [operState], reason: hardware-failure[transport] port [portId] on fabric interconnect [id] oper state: [operState], reason: hardware-failure | major | port-failed | This fault is raised on fabric interconnect ports and server-facing ports on an IOM or a FEX module when the system detects a hardware failure. | If you see this fault, create a show tech-support file for Cisco UCS Manager and the chassis or FEX module, and then contact Cisco TAC. | diagnostic | TRUE | network | port:PIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 278 | fltPortPIoHardwareFailure
F0279 | fltPortPIoSfp-not-present | [transport] port [portId] on chassis [id] oper state: [operState][transport] port [portId] on fabric interconnect [id] oper state: [operState] | info | port-failed | When a fabric interconnect port is not in an unconfigured state, an SFP is required for its operation. This fault is raised to indicate that the SFP is missing from a configured port. | If you see this fault, insert a supported SFP into the port on the fabric interconnect. A list of supported SFPs can be found on www.Cisco.com. | none | TRUE | network | port:PIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 279 | fltPortPIoSfpNotPresent
F0282 | fltFabricExternalPcDown | [type] port-channel [portId] on fabric interconnect [id] oper state: [operState], reason: [stateQual][type] port-channel [portId] on fabric interconnect [id] oper state: [operState], reason: [stateQual] | major | operational-state-down | This fault typically occurs when a fabric interconnect reports that a fabric port channel is operationally down. | If you see this fault, take the following actions: - Verify that the member ports in the fabric port channel are administratively up and operational. Check the link connectivity for each port. - If connectivity seems correct, check the operational states on the peer switch ports of the port channel members. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:ExternalPc |  | 282 | fltFabricExternalPcDown
F0283 | fltDcxVcDown | [transport] VIF [chassisId] / [slotId] [switchId]-[id] down, reason: [stateQual][transport] VIF [chassisId] / [id] [switchId]-[id] down, reason: [stateQual] | major | link-down | This fault typically occurs when a fabric interconnect reports one of the following connectivity states for a virtual interface: - Down - Errored - Unavailable | If you see this fault, take the following actions: - Verify that the uplink physical interface is up. - If the vNIC/vHBA is configured for a pin group, verify that the pin group targets are configured correctly. - In the Network Control Policy for the vNIC, verify that the 'Action on Uplink Fail' field is set to 'warning'. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | dcx:Vc | sys/chassis-[id]/blade-[slotId]/fabric-[switchId]/vc-[id] | 283 | fltDcxVcDown
F0291 | fltNetworkElementInoperable | Fabric Interconnect [id] operability: [operability] | critical | equipment-inoperable | This fault typically occurs when the fabric interconnect cluster controller reports that the membership state of the fabric interconnect is down, indicating that the fabric interconnect is inoperable. | If you see this fault, take the following actions: - Verify that both fabric interconnects in the cluster are running the same Kernel and System software versions. - Verify that the fabric interconnects software version and the Cisco UCS Manager software versions are the same. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | network:Element | sys/switch-[id] | 291 | fltNetworkElementInoperable
F0293 | fltMgmtEntityDegraded | Fabric Interconnect [id], HA Cluster interconnect link failure | major | link-down | This fault occurs when one of the cluster links (either L1 or L2) of a fabric interconnect is not operationally up. This issue impacts the full HA functionality of the fabric interconnect cluster. | If you see this fault, take the following actions: - Verify that both L1 and L2 links are properly connected between the fabric interconnects. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | network | mgmt:Entity | sys/mgmt-entity-[id] | 293 | fltMgmtEntityDegraded
F0294 | fltMgmtEntityDown | Fabric Interconnect [id], HA Cluster interconnect total link failure | critical | link-down | This fault occurs when both cluster links (L1 and L2) of the fabric interconnects are in a link-down state. This issue impacts the full HA functionality of the fabric interconnect cluster. | If you see this fault, take the following actions: - Verify that both L1 and L2 links are properly connected between the fabric interconnects. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | network | mgmt:Entity | sys/mgmt-entity-[id] | 294 | fltMgmtEntityDown
F0304 | fltDcxNsFailed | Server [chassisId]/[slotId] (service profile: [assignedToDn]) virtual network interface allocation failed.Server [id] (service profile: [assignedToDn]) virtual network interface allocation failed. | major | insufficient-resources | The adapter's vif-namespace activation failed due to insufficient resources. Cisco UCS Manager raises this fault when the number of deployed VIF resources exceeds the maximum VIF resources available on the adapter connected to the fabric interconnect. | If you see this fault, take the following actions: - Check the NS "size" and "used" resources to determine by how many vNICs the adapter exceeded the maximum. - Unconfigure or delete all vNICs on the adapter above the maximum number. - Add additional fabric uplinks from the IOM to the corresponding fabric interconnect and reacknowledge the chassis. This increases the "NS size" on the adapter. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | dcx:Ns | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/dcxns-[switchId] | 304 | fltDcxNsFailed
F0305 | fltComputePhysicalInsufficientlyEquipped | Server [id] (service profile: [assignedToDn]) has insufficient number of DIMMs, CPUs and/or adaptersServer [chassisId]/[slotId] (service profile: [assignedToDn]) has insufficient number of DIMMs, CPUs and/or adapters | minor | insufficiently-equipped | This fault typically occurs because Cisco UCS Manager has detected that the server has an insufficient number of DIMMs, CPUs, and/or adapters. | If you see this fault, take the following actions: - Verify that the DIMMs are installed in a supported configuration. - Verify that an adapter and CPU are installed. - Reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | compute:Physical |  | 305 | fltComputePhysicalInsufficientlyEquipped
F0306 | fltComputePhysicalIdentityUnestablishable | Server [id] (service profile: [assignedToDn]) has an invalid FRUServer [chassisId]/[slotId] (service profile: [assignedToDn]) has an invalid FRU | minor | identity-unestablishable | This fault typically occurs because Cisco UCS Manager has detected an unsupported server or CPU. | If you see this fault, take the following actions: - Verify that a supported server and/or CPU is installed. - Verify that the Cisco UCS Manager capability catalog is up to date. - Reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | compute:Physical |  | 306 | fltComputePhysicalIdentityUnestablishable
F0310 | fltComputeBoardPowerError | Motherboard of server [chassisId]/[slotId] (service profile: [assignedToDn]) power: [operPower]Motherboard of server [id] (service profile: [assignedToDn]) power: [operPower] | major | power-problem | This fault typically occurs when the server power sensors have detected a problem. | If you see this fault, take the following actions: - Make sure that the server is correctly installed in the chassis and that all cables are secure. - If you reinstalled the server, reacknowledge it. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | compute:Board | sys/chassis-[id]/blade-[slotId]/board | 310 | fltComputeBoardPowerError
F0311 | fltComputePhysicalPowerProblem | Server [id] (service profile: [assignedToDn]) oper state: [operState]Server [chassisId]/[slotId] (service profile: [assignedToDn]) oper state: [operState] | major | power-problem | This fault typically occurs when the server power sensors have detected a problem. | If you see this fault, take the following actions: - Make sure that the server is correctly installed in the chassis and that all cables are secure. - If you reinstalled the server, reacknowledge it. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | compute:Physical |  | 311 | fltComputePhysicalPowerProblem
F0312 | fltComputePhysicalThermalProblem | Server [id] (service profile: [assignedToDn]) oper state: [operState]Server [chassisId]/[slotId] (service profile: [assignedToDn]) oper state: [operState] | minor | thermal-problem | This fault typically occurs when the server thermal sensors have detected a problem. | If you see this fault, take the following actions: - Make sure that the server fans are working properly. - Wait for 24 hours to see if the problem resolves itself. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | compute:Physical |  | 312 | fltComputePhysicalThermalProblem
F0313 | fltComputePhysicalBiosPostTimeout | Server [id] (service profile: [assignedToDn]) BIOS failed power-on self testServer [chassisId]/[slotId] (service profile: [assignedToDn]) BIOS failed power-on self test | critical | equipment-inoperable | This fault typically occurs when the server has encountered a diagnostic failure. | If you see this fault, take the following actions: - Check the POST results for the server. In Cisco UCS Manager GUI, you can access the POST results from the General tab for the server. In Cisco UCS Manager CLI, you can access the POST results through the show post command under the scope for the server. - Reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | compute:Physical |  | 313 | fltComputePhysicalBiosPostTimeout
F0314 | fltComputePhysicalDiscoveryFailed | Server [id] (service profile: [assignedToDn]) discovery: [discovery]Server [chassisId]/[slotId] (service profile: [assignedToDn]) discovery: [discovery] | major | discovery-failed | This fault typically occurs for one of the following reasons: - The shallow discovery that occurs when the server associated with service profile failed. - The server is down. - The data path is not working. - Cisco UCS Manager cannot communicate with the CIMC on the server. - The server cannot communicate with the fabric interconnect. | If you see this fault, take the following actions: - Check the FSM tab and the current state of the server and any FSM operations. - Check the error descriptions and see if any server components indicate a failure. - If the server or a server component has failed, do the following: - Check the operational state of the server. - If the server is not operable, re-acknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | operational | compute:Physical |  | 314 | fltComputePhysicalDiscoveryFailed
F0315 | fltComputePhysicalAssociationFailed | Service profile [assignedToDn] failed to associate with server [id]Service profile [assignedToDn] failed to associate with server [chassisId]/[slotId] | critical | association-failed | This fault typically occurs for one of the following reasons: - The service profile could not be associated with the server. - The server is down. - The data path is not working. - Cisco UCS Manager cannot communicate with one or more of the fabric interconnect, the server, or a component on the server. | If you see this fault, take the following actions: - Check the FSM tab and the current state of the server and any FSM operations. - If the server is stuck in an inappropriate state, such as booting, power cycle the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | configuration | compute:Physical |  | 315 | fltComputePhysicalAssociationFailed
F0317 | fltComputePhysicalInoperable | Server [id] (service profile: [assignedToDn]) health: [operability]Server [chassisId]/[slotId] (service profile: [assignedToDn]) health: [operability] | major | equipment-inoperable | This fault typically occurs when the server has encountered a diagnostic failure. | If you see this fault, take the following actions: - Check the POST results for the server. In Cisco UCS Manager GUI, you can access the POST results from the General tab for the server. In Cisco UCS Manager CLI, you can access the POST results through the show post command under the scope for the server. - Reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | compute:Physical |  | 317 | fltComputePhysicalInoperable
F0318 | fltComputePhysicalUnassignedMissing | Server [id] (no profile) missingServer [chassisId]/[slotId] (no profile) missing | minor | equipment-missing | This fault typically occurs when the server, which is not associated with a service profile, was previously physically inserted in the slot, but cannot be detected by Cisco UCS Manager. | If you see this fault, take the following actions: - If the server is physically present in the slot, remove and then reinsert it. - If the server is not physically present in the slot, insert it. - Reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | compute:Physical |  | 318 | fltComputePhysicalUnassignedMissing
F0319 | fltComputePhysicalAssignedMissing | Server [id] (service profile: [assignedToDn]) missingServer [chassisId]/[slotId] (service profile: [assignedToDn]) missing | major | equipment-missing | This fault typically occurs when the server, which is associated with a service profile, was previously physically inserted in the slot, but cannot be detected by Cisco UCS Manager. | If you see this fault, take the following actions: - If the server is physically present in the slot, remove and then reinsert it. - If the server is not physically present in the slot, reinsert it. - Reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | compute:Physical |  | 319 | fltComputePhysicalAssignedMissing
F0320 | fltComputePhysicalUnidentified | Server [id] (service profile: [assignedToDn]) has an invalid FRU: [presence]Server [chassisId]/[slotId] (service profile: [assignedToDn]) has an invalid FRU: [presence] | minor | identity-unestablishable | This fault typically occurs because Cisco UCS Manager has detected an unsupported server or CPU. | If you see this fault, take the following actions: - Verify that a supported server and/or CPU is installed. - Verify that the Cisco UCS Manager capability catalog is up to date. - Reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | compute:Physical |  | 320 | fltComputePhysicalUnidentified
F0321 | fltComputePhysicalUnassignedInaccessible | Server [id] (no profile) inaccessibleServer [chassisId]/[slotId] (no profile) inaccessible | warning | equipment-inaccessible | This fault typically occurs when the server, which is not associated with a service profile, has lost connection to the fabric interconnects. This fault occurs if there are communication issues between the server CIMC and the fabric interconnects. | If you see this fault, take the following actions: - Wait a few minutes to see if the fault clears. This is typically a temporary issue, and can occur after a firmware upgrade. - If the fault does not clear after a brief time, remove the server and then reinsert it. - Reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | compute:Physical |  | 321 | fltComputePhysicalUnassignedInaccessible
F0322 | fltComputePhysicalAssignedInaccessible | Server [id] (service profile: [assignedToDn]) inaccessibleServer [chassisId]/[slotId] (service profile: [assignedToDn]) inaccessible | minor | equipment-inaccessible | This fault typically occurs when the server, which is associated with a service profile, has lost connection to the fabric interconnects. This fault occurs if there are communication issues between the server CIMC and the fabric interconnects. | If you see this fault, take the following actions: - Wait a few minutes to see if the fault clears. This is typically a temporary issue, and can occur after a firmware upgrade. - If the fault does not clear after a brief time, remove the server and then reinsert it. - Reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | compute:Physical |  | 322 | fltComputePhysicalAssignedInaccessible
F0324 | fltLsServerFailed | Service profile [name] failed | major | server-failed | Server has failed. This fault typically occurs if the adapter power on self-test results in major and critical errors. | If you see this fault, take the following actions: - Check the POST results for the server. In Cisco UCS Manager GUI, you can access the POST results from the General tab for the server. In Cisco UCS Manager CLI, you can access the POST results through the show post command under the scope for the server. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | ls:Server | org-[name]/tier-[name]/ls-[name] | 324 | fltLsServerFailed
F0326 | fltLsServerDiscoveryFailed | Service profile [name] discovery failed | major | discovery-failed | The shallow discovery that occurs when the server associated with service profile fails. If the server is up and the data path is working, this fault typically occurs as a result of one of the following issues: - Cisco UCS Manager cannot communicate with the CIMC on the server. - The server cannot communicate with the fabric interconnect. | If you see this fault, take the following actions: - Check the FSM tab and view the current state of the server and any FSM operations. - Check the error descriptions and see if any server components indicate a failure. - If the server or a server component has failed, do the following: type="a" - Check the operational state of the server. - If the server is not operable, reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | ls:Server | org-[name]/tier-[name]/ls-[name] | 326 | fltLsServerDiscoveryFailed
F0327 | fltLsServerConfigFailure | Service profile [name] configuration failed due to [configQualifier] | major | configuration-failure | The named configuration qualifier is not available. This fault typically occurs because Cisco UCS Manager cannot successfully deploy the service profile due to a lack of resources that meet the named qualifier. For example, this fault can occur if the following occurs: - The service profile is configured for a server adapter with vHBAs, and the adapter on the server does not support vHBAs. - The service profile is created from a template which includes a server pool, and the server pool is empty. - The local disk configuration policy in the service profile specifies the No Local Storage mode, but the server contains local disks. | If you see this fault, take the following actions: - Check the status of the server pool associated with the service profile. If the pool is empty, add more blade servers to it. - Check the state of the server and ensure that it is in either the discovered or unassociated state. - If the server is associated or undiscovered, do one of the following: - Discover the server. - Disassociate the server from the current service profile. - Select another server to associate with the service profile. - Review each policy in the service profile and verify that the selected server meets the requirements in the policy. - If the server does not meet the requirements of the service profile, do one of the following: - Modify the service profile to match the server. - Select another server that does meet the requirements to associate with the service profile. - If you can verify that the server meets the requirements of the service profile, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | server | ls:Server | org-[name]/tier-[name]/ls-[name] | 327 | fltLsServerConfigFailure
F0329 | fltLsServerMaintenanceFailed | Service profile [name] maintenance failed | major | maintenance-failed | Cisco UCS Manager currently does not use this fault. | If you see this fault, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | ls:Server | org-[name]/tier-[name]/ls-[name] | 329 | fltLsServerMaintenanceFailed
F0330 | fltLsServerRemoved | Service profile [name] underlying resource removed | major | equipment-removed | Cisco UCS Manager cannot access the server associated with the service profile. This fault typically occurs as a result of one of the following issues: - The server has been physically removed from the slot. - The server is not available. | If you see this fault, take the following actions: - If the server was removed from the slot, reinsert the server in the slot. - If the server was not removed, remove and reinsert the server. NOTE: If the server is operable, this action can be disruptive to current operations. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | ls:Server | org-[name]/tier-[name]/ls-[name] | 330 | fltLsServerRemoved
F0331 | fltLsServerInaccessible | Service profile [name] cannot be accessed | major | server-inaccessible | Cisco UCS Manager cannot communicate with the CIMC on the server. This fault typically occurs as a result of one of the following issues: - The server port or ports have failed. - The I/O module is offline. - The BMC has failed. | If you see this fault, take the following actions: - If Cisco UCS Manager shows that the CIMC is down, physically reseat the server. - If Cisco UCS Manager shows that the server ports have failed, attempt to enable them. - If the I/O module is offline, check for faults on that component. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | ls:Server | org-[name]/tier-[name]/ls-[name] | 331 | fltLsServerInaccessible
F0332 | fltLsServerAssociationFailed | Service profile [name] association failed for [pnDn] | major | association-failed | The service profile could not be associated with the server. This fault typically occurs because Cisco UCS Manager cannot communicate with one or more of the following: - Fabric interconnect - CIMC on the server - SAS controller driver - Server | If you see this fault, take the following actions: - Check the FSM tab for the server and service profile to determine why the association failed. - If the server is stuck in an inappropriate state, such as booting, power cycle the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | server | ls:Server | org-[name]/tier-[name]/ls-[name] | 332 | fltLsServerAssociationFailed
F0334 | fltLsServerUnassociated | Service profile [name] is not associated | warning | unassociated | The service profile has not yet been associated with a server or a server pool. This fault typically occurs as a result of one of the following issues: - There is no acceptable server in the server pool. - The association failed. | If you see this fault, take the following actions: - If you did not intend to associate the service profile, ignore the fault. - If you did intend to associate the service profile, check the association failure fault. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | ls:Server | org-[name]/tier-[name]/ls-[name] | 334 | fltLsServerUnassociated
F0337 | fltLsServerServer-unfulfilled | Server [pnDn] does not fulfill Service profile [name] due to [configQualifier] | warning | server-failed | The server no longer meets the qualification requirements of the service profile. This fault typically occurs as a result of one of the following issues: - The server has been physically changed. - A required component of the server has failed. | If you see this fault, take the following actions: - Check the server inventory compare to the service profile qualifications. - If the server inventory does not match the service profile qualifications, do one of the following: - Associate the server with a different service profile. - Ensure the server has sufficient resources to qualify for the current service profile. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | ls:Server | org-[name]/tier-[name]/ls-[name] | 337 | fltLsServerServerUnfulfilled
F0367 | fltEtherSwitchIntFIoSatellite-connection-absent | No link between IOM port [chassisId]/[slotId]/[portId] and fabric interconnect [switchId]:[peerSlotId]/[peerPortId] | major | satellite-connection-absent | This fault is raised when an I/O module fabric port, which links the I/O module port and the fabric interconnect, is not functional | If you see this fault, take the following actions: - Verify the fabric interconnect-chassis topology. Make sure each I/O module is connected to only one fabric interconnect. - Ensure that the fabric interconnect server port is configured and enabled. - Ensure that the links are plugged in properly and reacknowledge the chassis. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | connectivity | ether:SwitchIntFIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 367 | fltEtherSwitchIntFIoSatelliteConnectionAbsent
F0368 | fltEtherSwitchIntFIoSatellite-wiring-problem | Invalid connection between IOM port [chassisId]/[slotId]/[portId] and fabric interconnect [switchId]:[peerSlotId]/[peerPortId] | info | satellite-mis-connected | This fault typically occurs as a result of a satellite wiring problem on the network-facing interface of an I/O module and Cisco UCS Manager detects that at least one IOM uplink is misconnected to one of the fabric interconnect ports.</br | If you see this fault, take the following actions: - Verify the fabric interconnect-chassis topology. Make sure each I/O module is connected to only one fabric interconnect. - Ensure that the links are plugged in properly and re-acknowledge the chassis. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | connectivity | ether:SwitchIntFIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 368 | fltEtherSwitchIntFIoSatelliteWiringProblem
F0369 | fltEquipmentPsuPowerSupplyProblem | Power supply [id] in chassis [id] power: [power]Power supply [id] in fabric interconnect [id] power: [power]Power supply [id] in fex [id] power: [power]Power supply [id] in server [id] power: [power] | major | power-problem | This fault typically occurs when Cisco UCS Manager detects a problem with a power supply unit in a chassis, fabric interconnect or a FEX. For example, the PSU is not functional. | If you see this fault, take the following actions: - Verify that the power cord is properly connected to the PSU and the power source. - Verify that the power source is 220 volts. - Verify that the PSU is properly installed in the chassis or fabric interconnect. - Remove the PSU and reinstall it. - Replace the PSU. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 369 | fltEquipmentPsuPowerSupplyProblem
F0371 | fltEquipmentFanDegraded | Fan [id] in Fan Module [tray]-[id] under chassis [id] operability: [operability]Fan [id] in fabric interconnect [id] operability: [operability]Fan [id] in fex [id] operability: [operability]Fan [id] in Fan Module [tray]-[id] under server [id] operability: [operability] | minor | equipment-degraded | This fault occurs when one or more fans in a fan module are not operational, but at least one fan is operational. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the fan module. - Review the Cisco UCS Site Preparation Guide and ensure the fan module has adequate airflow, including front and back clearance. - Verify that the air flows are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Replace the faulty fan modules. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:Fan | sys/rack-unit-[id]/fan-module-[tray]-[id]/fan-[id] | 371 | fltEquipmentFanDegraded
F0373 | fltEquipmentFanInoperable | Fan [id] in Fan Module [tray]-[id] under chassis [id] operability: [operability]Fan [id] in fabric interconnect [id] operability: [operability]Fan [id] in fex [id] operability: [operability]Fan [id] in Fan Module [tray]-[id] under server [id] operability: [operability] | major | equipment-inoperable | This fault occurs if a fan is not operational. | If you see this fault, take the following actions: - Remove fan module and re-install the fan module again. Remove only one fan module at a time. - Replace fan module with a different fan module - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | equipment | equipment:Fan | sys/rack-unit-[id]/fan-module-[tray]-[id]/fan-[id] | 373 | fltEquipmentFanInoperable
F0374 | fltEquipmentPsuInoperable | Power supply [id] in chassis [id] operability: [operability]Power supply [id] in fabric interconnect [id] operability: [operability]Power supply [id] in fex [id] operability: [operability]Power supply [id] in server [id] operability: [operability] | major | equipment-inoperable | This fault typically occurs when Cisco UCS Manager detects a problem with a power supply unit in a chassis, fabric interconnect or a FEX. For example, the PSU is not functional. | If you see this fault, take the following actions: - Verify that the power cord is properly connected to the PSU and the power source. - Verify that the power source is 220 volts. - Verify that the PSU is properly installed in the chassis or fabric interconnect. - Remove the PSU and reinstall it. - Replace the PSU. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | equipment | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 374 | fltEquipmentPsuInoperable
F0376 | fltEquipmentIOCardRemoved | [side] IOM [chassisId]/[id] ([switchId]) is removed | critical | equipment-removed | This fault typically occurs because an I/O module is removed from the chassis. In a cluster configuration, the chassis fails over to the other I/O module. For a standalone configuration, the chassis associated with the I/O module loses network connectivity. This is a critical fault because it can result in the loss of network connectivity and disrupt data traffic through the I/O module. | If you see this fault, take the following actions: - Reinsert the I/O module and configure the fabric-interconnect ports connected to it as server ports and wait a few minutes to see if the fault clears. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:IOCard | sys/chassis-[id]/slot-[id] | 376 | fltEquipmentIOCardRemoved
F0377 | fltEquipmentFanModuleMissing | Fan module [tray]-[id] in chassis [id] presence: [presence]Fan module [tray]-[id] in server [id] presence: [presence]Fan module [tray]-[id] in fabric interconnect [id] presence: [presence] | warning | equipment-missing | This fault occurs if a fan Module slot is not equipped or removed from its slot | If you see this fault, take the following actions: - If the reported slot is empty, insert a fan module into the slot. - If the reported slot contains a fan module, remove and reinsert the fan module. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:FanModule | sys/rack-unit-[id]/fan-module-[tray]-[id] | 377 | fltEquipmentFanModuleMissing
F0378 | fltEquipmentPsuMissing | Power supply [id] in chassis [id] presence: [presence]Power supply [id] in fabric interconnect [id] presence: [presence]Power supply [id] in fex [id] presence: [presence]Power supply [id] in server [id] presence: [presence] | warning | equipment-missing | This fault typically occurs when Cisco UCS Manager detects a problem with a power supply unit in a chassis, fabric interconnect, or a FEX. For example, the PSU is missing. | If you see this fault, take the following actions: - If the PSU is physically present in the slot, remove and then reinsert it. - If the PSU is not physically present in the slot, insert a new PSU. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 378 | fltEquipmentPsuMissing
F0379 | fltEquipmentIOCardThermalProblem | [side] IOM [chassisId]/[id] ([switchId]) operState: [operState] | major | thermal-problem | This fault occurs when there is a thermal problem on an I/O module. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the I/O module. - Review the Cisco UCS Site Preparation Guide to ensure the I/O modules have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Replace faulty I/O modules. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:IOCard | sys/chassis-[id]/slot-[id] | 379 | fltEquipmentIOCardThermalProblem
F0380 | fltEquipmentFanModuleThermalThresholdNonCritical | Fan module [tray]-[id] in chassis [id] temperature: [thermal]Fan module [tray]-[id] in server [id] temperature: [thermal]Fan module [tray]-[id] in fabric interconnect [id] temperature: [thermal] | minor | thermal-problem | This fault occurs when the temperature of a fan module has exceeded a non-critical threshold value, but is still below the critical threshold. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the fan module. - Review the Cisco UCS Site Preparation Guide to ensure the fan modules have adequate airflow, including front and back clearance. - Verify that the air flows are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Replace faulty fan modules. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:FanModule | sys/rack-unit-[id]/fan-module-[tray]-[id] | 380 | fltEquipmentFanModuleThermalThresholdNonCritical
F0381 | fltEquipmentPsuThermalThresholdNonCritical | Power supply [id] in chassis [id] temperature: [thermal]Power supply [id] in fabric interconnect [id] temperature: [thermal]Power supply [id] in server [id] temperature: [thermal] | minor | thermal-problem | This fault occurs when the temperature of a PSU module has exceeded a non-critical threshold value, but is still below the critical threshold. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the PSU module. - Review the Cisco UCS Site Preparation Guide to ensure the PSU modules have adequate airflow, including front and back clearance. - Verify that the air flows are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Replace faulty PSU modules. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 381 | fltEquipmentPsuThermalThresholdNonCritical
F0382 | fltEquipmentFanModuleThermalThresholdCritical | Fan module [tray]-[id] in chassis [id] temperature: [thermal]Fan module [tray]-[id] in server [id] temperature: [thermal]Fan module [tray]-[id] in fabric interconnect [id] temperature: [thermal] | major | thermal-problem | This fault occurs when the temperature of a fan module has exceeded a critical threshold value. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the fan module. - Review the Cisco UCS Site Preparation Guide to ensure the fan modules have adequate airflow, including front and back clearance. - Verify that the air flows are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Replace faulty fan modules. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:FanModule | sys/rack-unit-[id]/fan-module-[tray]-[id] | 382 | fltEquipmentFanModuleThermalThresholdCritical
F0383 | fltEquipmentPsuThermalThresholdCritical | Power supply [id] in chassis [id] temperature: [thermal]Power supply [id] in fabric interconnect [id] temperature: [thermal]Power supply [id] in server [id] temperature: [thermal] | major | thermal-problem | This fault occurs when the temperature of a PSU module has exceeded a critical threshold value. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the PSU module. - Review the Cisco UCS Site Preparation Guide to ensure the PSU modules have adequate airflow, including front and back clearance. - Verify that the air flows are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Replace faulty PSU modules. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 383 | fltEquipmentPsuThermalThresholdCritical
F0384 | fltEquipmentFanModuleThermalThresholdNonRecoverable | Fan module [tray]-[id] in chassis [id] temperature: [thermal]Fan module [tray]-[id] in server [id] temperature: [thermal]Fan module [tray]-[id] in fabric interconnect [id] temperature: [thermal] | critical | thermal-problem | This fault occurs when the temperature of a fan module has been out of operating range, and the issue is not recoverable. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the fan module. - Review the Cisco UCS Site Preparation Guide to ensure the fan modules have adequate airflow, including front and back clearance. - Verify that the air flows are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Replace faulty fan modules. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:FanModule | sys/rack-unit-[id]/fan-module-[tray]-[id] | 384 | fltEquipmentFanModuleThermalThresholdNonRecoverable
F0385 | fltEquipmentPsuThermalThresholdNonRecoverable | Power supply [id] in chassis [id] temperature: [thermal]Power supply [id] in fabric interconnect [id] temperature: [thermal]Power supply [id] in server [id] temperature: [thermal] | critical | thermal-problem | This fault occurs when the temperature of a PSU module has been out of operating range, and the issue is not recoverable. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the PSU module. - Review the Cisco UCS Site Preparation Guide to ensure the PSU modules have adequate airflow, including front and back clearance. - Verify that the air flows are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Replace faulty PSU modules. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 385 | fltEquipmentPsuThermalThresholdNonRecoverable
F0387 | fltEquipmentPsuVoltageThresholdNonCritical | Power supply [id] in chassis [id] voltage: [voltage]Power supply [id] in fabric interconnect [id] voltage: [voltage]Power supply [id] in fex [id] voltage: [voltage]Power supply [id] in server [id] voltage: [voltage] | minor | voltage-problem | This fault occurs when the PSU voltage is out of normal operating range, but hasn't reached to a critical stage yet. Normally the PSU will recover itself from this situation. | If you see this fault, take the following actions: - Monitor the PSU for further degradation. - Remove and reseat the PSU. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 387 | fltEquipmentPsuVoltageThresholdNonCritical
F0389 | fltEquipmentPsuVoltageThresholdCritical | Power supply [id] in chassis [id] voltage: [voltage]Power supply [id] in fabric interconnect [id] voltage: [voltage]Power supply [id] in fex [id] voltage: [voltage]Power supply [id] in server [id] voltage: [voltage] | major | voltage-problem | This fault occurs when the PSU voltage has exceeded the specified hardware voltage rating. | If you see this fault, take the following actions: - Remove and reseat the PSU. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 389 | fltEquipmentPsuVoltageThresholdCritical
F0391 | fltEquipmentPsuVoltageThresholdNonRecoverable | Power supply [id] in chassis [id] voltage: [voltage]Power supply [id] in fabric interconnect [id] voltage: [voltage]Power supply [id] in fex [id] voltage: [voltage]Power supply [id] in server [id] voltage: [voltage] | critical | voltage-problem | This fault occurs when the PSU voltage has exceeded the specified hardware voltage rating and PSU hardware may have been damaged as a result or may be at risk of being damaged. | If you see this fault, take the following actions: - Remove and reseat the PSU. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 391 | fltEquipmentPsuVoltageThresholdNonRecoverable
F0392 | fltEquipmentPsuPerfThresholdNonCritical | Power supply [id] in chassis [id] output power: [perf]Power supply [id] in fabric interconnect [id] output power: [perf]Power supply [id] in server [id] output power: [perf] | minor | performance-problem | This fault is raised as a warning if the current output of the PSU in a chassis, fabric interconnect, or rack server does not match the desired output value. | If you see this fault, take the following actions: - Monitor the PSU status. - If possible, remove and reseat the PSU. - If the above action did not resolve the issue, create a show tech-support file for the chassis and Cisco UCS Manager, and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 392 | fltEquipmentPsuPerfThresholdNonCritical
F0393 | fltEquipmentPsuPerfThresholdCritical | Power supply [id] in chassis [id] output power: [perf]Power supply [id] in fabric interconnect [id] output power: [perf]Power supply [id] in server [id] output power: [perf] | major | performance-problem | This fault occurs if the current output of the PSU in a chassis, fabric interconnect, or rack server is far below or above the desired output value. | If you see this fault, take the following actions: - Monitor the PSU status. - Plan to replace the PSU as soon as possible. - If the above actions did not resolve the issue, create a show tech-support file for the chassis and Cisco UCS Manager, and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 393 | fltEquipmentPsuPerfThresholdCritical
F0394 | fltEquipmentPsuPerfThresholdNonRecoverable | Power supply [id] in chassis [id] output power: [perf]Power supply [id] in fabric interconnect [id] output power: [perf]Power supply [id] in server [id] output power: [perf] | critical | performance-problem | This fault occurs if the current output of the PSU in a chassis, fabric interconnect, or rack server is far above or below the non-recoverable threshold value. | If you see this fault, plan to replace the PSU as soon as possible. | diagnostic | TRUE | equipment | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 394 | fltEquipmentPsuPerfThresholdNonRecoverable
F0395 | fltEquipmentFanPerfThresholdNonCritical | Fan [id] in Fan Module [tray]-[id] under chassis [id] speed: [perf]Fan [id] in fabric interconnect [id] speed: [perf]Fan [id] in Fan Module [tray]-[id] under server [id] speed: [perf] | info | performance-problem | This fault occurs when the fan speed reading from the fan controller does not match the desired fan speed and is outside of the normal operating range. This can indicate a problem with a fan or with the reading from the fan controller. | If you see this fault, take the following actions: - Monitor the fan status. - If the problem persists for a long period of time or if other fans do not show the same problem, reseat the fan. - Replace the fan module. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Fan | sys/rack-unit-[id]/fan-module-[tray]-[id]/fan-[id] | 395 | fltEquipmentFanPerfThresholdNonCritical
F0396 | fltEquipmentFanPerfThresholdCritical | Fan [id] in Fan Module [tray]-[id] under chassis [id] speed: [perf]Fan [id] in fabric interconnect [id] speed: [perf]Fan [id] in Fan Module [tray]-[id] under server [id] speed: [perf] | info | performance-problem | This fault occurs when the fan speed read from the fan controller does not match the desired fan speed and has exceeded the critical threshold and is in risk of failure. This can indicate a problem with a fan or with the reading from the fan controller. | If you see this fault, take the following actions: - Monitor the fan status. - If the problem persists for a long period of time or if other fans do not show the same problem, reseat the fan. - If the above actions did not resolve the issue, create a show tech-support file for the chassis and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Fan | sys/rack-unit-[id]/fan-module-[tray]-[id]/fan-[id] | 396 | fltEquipmentFanPerfThresholdCritical
F0397 | fltEquipmentFanPerfThresholdNonRecoverable | Fan [id] in Fan Module [tray]-[id] under chassis [id] speed: [perf]Fan [id] in fabric interconnect [id] speed: [perf]Fan [id] in Fan Module [tray]-[id] under server [id] speed: [perf] | info | performance-problem | This fault occurs when the fan speed read from the fan controller has far exceeded the desired fan speed. It frequently indicates that the fan has failed. | If you see this fault, take the following actions: - Replace the fan. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Fan | sys/rack-unit-[id]/fan-module-[tray]-[id]/fan-[id] | 397 | fltEquipmentFanPerfThresholdNonRecoverable
F0398 | fltEquipmentIOCardFirmwareUpgrade | Chassis controller in IOM [chassisId]/[id] ([switchId]) firmware upgrade problem: [upgradeStatus] | major | firmware-upgrade-problem | This fault typically occurs when an IOM upgrade fails. | If you see this fault, take the following actions: - On the FSM tab for the IOM, verify whether FSM for the upgrade completed successfully or failed. - If the FSM failed, review the error message in the FSM. - If the error message is self explanatory, verify the physical connectivity. For example, an error message could be No Connection to Endpoint or Link Down. - If the above action did not resolve the issue and the fault persists, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:IOCard | sys/chassis-[id]/slot-[id] | 398 | fltEquipmentIOCardFirmwareUpgrade
F0399 | fltEquipmentChassisUnsupportedConnectivity | Current connectivity for chassis [id] does not match discovery policy: [configState] | major | unsupported-connectivity-configuration | This fault typically occurs when the current connectivity for a chassis does not match the configuration in the chassis discovery policy. | If you see this fault, take the following actions: - Verify that the correct number of links are configured in the chassis discovery policy. - Check the state of the I/O module links. - Reacknowledge the chassis. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | connectivity | equipment:Chassis | sys/chassis-[id] | 399 | fltEquipmentChassisUnsupportedConnectivity
F0400 | fltEquipmentChassisUnacknowledged | Chassis [id] connectivity configuration: [configState] | warning | equipment-unacknowledged | This fault typically occurs when or more of the I/O module links from the chassis are unacknowledged. | If you see this fault, take the following actions: - Check the state of the I/O module links. - Reacknowledge the chassis. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | connectivity | equipment:Chassis | sys/chassis-[id] | 400 | fltEquipmentChassisUnacknowledged
F0401 | fltEquipmentIOCardUnsupportedConnectivity | IOM [chassisId]/[id] ([switchId]) current connectivity does not match discovery policy: [configState] | major | unsupported-connectivity-configuration | This fault typically occurs when the current connectivity for an I/O module does not match the configuration in the chassis discovery policy. | If you see this fault, take the following actions: - Verify that the correct number of links are configured in the chassis discovery policy. - Check the state of the I/O module links. - Reacknowledge the chassis. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | connectivity | equipment:IOCard | sys/chassis-[id]/slot-[id] | 401 | fltEquipmentIOCardUnsupportedConnectivity
F0402 | fltEquipmentIOCardUnacknowledged | IOM [chassisId]/[id] ([switchId]) connectivity configuration: [configState] | warning | equipment-unacknowledged | This fault typically occurs when an I/O module is unacknowledged. | If you see this fault, take the following actions: - Check the state of the I/O module links. - Reacknowledge the chassis. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | connectivity | equipment:IOCard | sys/chassis-[id]/slot-[id] | 402 | fltEquipmentIOCardUnacknowledged
F0403 | fltEquipmentIOCardPeerDisconnected | IOM [chassisId]/[id] ([switchId]) peer connectivity: [peerCommStatus] | warning | equipment-disconnected | This fault typically occurs when an I/O module is unable to communicate with its peer I/O module. | If you see this fault, take the following actions: - Wait a few minutes to see if the fault clears. This is typically a temporary issue, and can occur after a firmware upgrade. - If the fault does not clear after a few minutes, remove and reinsert the I/O module. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | connectivity | equipment:IOCard | sys/chassis-[id]/slot-[id] | 403 | fltEquipmentIOCardPeerDisconnected
F0404 | fltEquipmentChassisIdentity | Chassis [id] has a mismatch between FRU identity reported by Fabric/IOM vs. FRU identity reported by CMC | critical | fru-problem | This fault typically occurs when the FRU information for an I/O module is corrupted or malformed. | If you see this fault, take the following actions: - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Chassis | sys/chassis-[id] | 404 | fltEquipmentChassisIdentity
F0405 | fltEquipmentIOCardIdentity | [side] IOM [chassisId]/[id] ([switchId]) has a malformed FRU | critical | fru-problem | This fault typically occurs when the FRU information for an I/O module is corrupted or malformed. | If you see this fault, take the following actions: - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:IOCard | sys/chassis-[id]/slot-[id] | 405 | fltEquipmentIOCardIdentity
F0406 | fltEquipmentFanModuleIdentity | Fan Module [tray]-[id] in chassis [id] has a malformed FRUFan Module [tray]-[id] in server [id] has a malformed FRUFan Module [tray]-[id] in fabric interconnect [id] has a malformed FRU | critical | fru-problem | This fault typically occurs when the FRU information for a fan module is corrupted or malformed. | If you see this fault, take the following actions: - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:FanModule | sys/rack-unit-[id]/fan-module-[tray]-[id] | 406 | fltEquipmentFanModuleIdentity
F0407 | fltEquipmentPsuIdentity | Power supply [id] on chassis [id] has a malformed FRUPower supply [id] on server [id] has a malformed FRU | critical | fru-problem | This fault typically occurs when the FRU information for a power supply unit is corrupted or malformed. | If you see this fault, take the following actions: - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 407 | fltEquipmentPsuIdentity
F0408 | fltEquipmentChassisPowerProblem | Power state on chassis [id] is [power] | major | power-problem | This fault typically occurs when the chassis fails to meet the minimal power requirements defined in the power policy or when one or more power supplies have failed. | If you see this fault, take the following actions: - In Cisco UCS Manager, verify that all PSUs for the chassis are functional. - Verify that all PSUs are seated properly within the chassis and are powered on. - Physically unplug and replug the power cord into the chassis. - If all PSUs are operating at maximum capacity, either add more PSUs to the chassis or redefine the power policy in Cisco UCS Manager. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Chassis | sys/chassis-[id] | 408 | fltEquipmentChassisPowerProblem
F0409 | fltEquipmentChassisThermalThresholdCritical | Thermal condition on chassis [id] cause: [thermalStateQualifier] | major | thermal-problem | This fault occurs under the following conditions: - If a component within a chassis is operating outside the safe thermal operating range. - If the chassis controller in the IOM is unable to determine the thermal condition of a blade server, the show tech-support file for the chassis provides a more detailed report of the most severe thermal conditions currently applicable for that chassis. | If you see this fault, take the following actions: - Check the temperature readings for the blade servers and IOM and ensure they are within the recommended thermal safe operating range. - If the fault reports a "Thermal Sensor threshold crossing in blade" error for one or more blade servers, check if DIMM or processor temperature related faults have been raised against that blade. - If the fault reports a "Thermal Sensor threshold crossing in IOM" error for one or both the IOMs, check if thermal faults have been raised against that IOM. Those faults include details of the thermal condition. - If the fault reports a "Missing or Faulty Fan" error, check on the status of that fan. If it needs replacement, create a show tech-support file for the chassis and contact Cisco TAC. - If the fault reports a "No connectivity between IOM and blade" or "Thermal Sensor readings unavailable from blade" error, check if that blade server is operational and whether any faults have been raised against that blade server. In this situation, the chassis controller may go into a fail-safe operating mode and the fan speeds may increase as a precautionary measure. - If the above actions did not resolve the issue and the condition persists, create a show tech-support file for Cisco UCS Manager and the chassis and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Chassis | sys/chassis-[id] | 409 | fltEquipmentChassisThermalThresholdCritical
F0410 | fltEquipmentChassisThermalThresholdNonCritical | Thermal condition on chassis [id] cause: [thermalStateQualifier] | minor | thermal-problem | UCSM raises this fault under the following conditions: - If a component within a chassis is operating outside the safe thermal operating range. - If the chassis controller in the IOM is unable to determine the thermal condition of a blade server, the show tech-support file for the chassis provides a more detailed report of the most severe thermal conditions currently applicable for that chassis. | If you see this fault, take the following actions: - Check the temperature readings for the blade servers and IOM and ensure they are within the recommended thermal safe operating range. - If the fault reports a "Thermal Sensor threshold crossing in blade" error for one or more blade servers, check if DIMM or processor temperature related faults have been raised against that blade. - If the fault reports a "Thermal Sensor threshold crossing in IOM" error for one or both the IOMs, check if thermal faults have been raised against that IOM. Those faults include details of the thermal condition. - If the fault reports a "Missing or Faulty Fan" error, check on the status of that fan. If it needs replacement, create a show tech-support file for the chassis and contact Cisco TAC. - If the fault reports a "No connectivity between IOM and blade" or "Thermal Sensor readings unavailable from blade" error, check if that blade server is operational and whether any faults have been raised against that blade server. In this situation, the chassis controller may go into a fail-safe operating mode and the fan speeds may increase as a precautionary measure. - If the above actions did not resolve the issue and the condition persists, create a show tech-support file for Cisco UCS Manager and the chassis and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Chassis | sys/chassis-[id] | 410 | fltEquipmentChassisThermalThresholdNonCritical
F0411 | fltEquipmentChassisThermalThresholdNonRecoverable | Thermal condition on chassis [id] cause:[thermalStateQualifier] | critical | thermal-problem | UCSM raises this fault under the following conditions: - If a component within a chassis is operating outside the safe thermal operating range. - If the chassis controller in the IOM is unable to determine the thermal condition of a blade server, the show tech-support file for the chassis provides a more detailed report of the most severe thermal conditions currently applicable for that chassis. | If you see this fault, take the following actions: - Check the temperature readings for the blade servers and IOM and ensure they are within the recommended thermal safe operating range. - If the fault reports a "Thermal Sensor threshold crossing in blade" error for one or more blade servers, check if DIMM or processor temperature related faults have been raised against that blade. - If the fault reports a "Thermal Sensor threshold crossing in IOM" error for one or both the IOMs, check if thermal faults have been raised against that IOM. Those faults include details of the thermal condition. - If the fault reports a "Missing or Faulty Fan" error, check on the status of that fan. If it needs replacement, create a show tech-support file for the chassis and contact Cisco TAC. - If the fault reports a "No connectivity between IOM and blade" or "Thermal Sensor readings unavailable from blade" error, check if that blade server is operational and whether any faults have been raised against that blade server. In this situation, the chassis controller may go into a fail-safe operating mode and the fan speeds may increase as a precautionary measure. - If the above actions did not resolve the issue and the condition persists, create a show tech-support file for Cisco UCS Manager and the chassis and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Chassis | sys/chassis-[id] | 411 | fltEquipmentChassisThermalThresholdNonRecoverable
F0424 | fltComputeBoardCmosVoltageThresholdCritical | Possible loss of CMOS settings: CMOS battery voltage on server [chassisId]/[slotId] is [cmosVoltage]Possible loss of CMOS settings: CMOS battery voltage on server [id] is [cmosVoltage] | minor | voltage-problem | This fault is raised when the CMOS battery voltage has dropped to lower than the normal operating range. This could impact the clock and other CMOS settings. | If you see this fault, replace the battery. | none | TRUE | environmental | compute:Board | sys/chassis-[id]/blade-[slotId]/board | 424 | fltComputeBoardCmosVoltageThresholdCritical
F0425 | fltComputeBoardCmosVoltageThresholdNonRecoverable | Possible loss of CMOS settings: CMOS battery voltage on server [chassisId]/[slotId] is [cmosVoltage]Possible loss of CMOS settings: CMOS battery voltage on server [id] is [cmosVoltage] | major | voltage-problem | This fault is raised when the CMOS battery voltage has dropped quite low and is unlikely to recover. This impacts the clock and other CMOS settings. | If you see this fault, replace the battery. | none | TRUE | environmental | compute:Board | sys/chassis-[id]/blade-[slotId]/board | 425 | fltComputeBoardCmosVoltageThresholdNonRecoverable
F0428 | fltMgmtEntityElection-failure | Fabric Interconnect [id], election of primary managemt instance has failed | critical | election-failure | This fault occurs in an unlikely event that the fabric interconnects in a cluster configuration could not reach an agreement for selecting the primary fabric interconnect. This impacts the full HA functionality of the fabric interconnect cluster. | If you see this fault, take the following actions: - Verify that the initial setup configuration is correct on both fabric interconnects. - Verify that the L1 and L2 links are properly connected between the fabric interconnects. - In the Cisco UCS Manager CLI, run the cluster force primary local-mgmt command on one fabric interconnect. - Reboot the fabric interconnects. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | management | mgmt:Entity | sys/mgmt-entity-[id] | 428 | fltMgmtEntityElectionFailure
F0429 | fltMgmtEntityHa-not-ready | Fabric Interconnect [id], HA functionality not ready | major | ha-not-ready | This fault occurs if Cisco UCS Manager cannot discover or communicate with one or more chassis or rack servers to write the HA Cluster state. This impacts the full HA functionality of the fabric interconnect cluster. | If you see this fault, take the following actions: - Verify that the initial setup configuration is correct on both fabric interconnects. - Verify that the L1 and L2 links are properly connected between the fabric interconnects. - Verify that the IOMs and/or FEXes are reachable and the server ports are enabled and operationally up. - Verify that the chassis and/or rack servers are powered up and reachable - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | mgmt:Entity | sys/mgmt-entity-[id] | 429 | fltMgmtEntityHaNotReady
F0430 | fltMgmtEntityVersion-incompatible | Fabric Interconnect [id], management services, incompatible versions | critical | version-incompatible | This fault occurs if the Cisco UCS Manager software on the subordinate fabric interconnect is not the same release as that of the primary fabric interconnect. This impacts the full HA functionality of the fabric interconnect cluster. | If you see this fault, take the following actions: - Upgrade the Cisco UCS Manager software on the subordinate fabric interconnect to the same release as the primary fabric interconnect and verify that both fabric interconnects are running the same release of Cisco UCS Manager. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | management | mgmt:Entity | sys/mgmt-entity-[id] | 430 | fltMgmtEntityVersionIncompatible
F0434 | fltEquipmentFanMissing | Fan [id] in fabric interconnect [id] presence: [presence]Fan [id] in fex [id] presence: [presence]Fan [id] in Fan Module [tray]-[id] under server [id] presence: [presence] | warning | equipment-missing | This fault occurs in the unlikely event that a fan in a fan module cannot be detected. | If you see this fault, take the following actions: - Insert/reinsert the fan module in the slot that is reporting the issue. - Replace the fan module with a different fan module, if available. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:Fan | sys/rack-unit-[id]/fan-module-[tray]-[id]/fan-[id] | 434 | fltEquipmentFanMissing
F0435 | fltEquipmentIOCardAutoUpgradingFirmware | IOM [chassisId]/[id] ([switchId]) is auto upgrading firmware | major | auto-firmware-upgrade | This fault typically occurs when an I/O module is auto upgrading. Auto-upgrade occurs when the firmware version on the IOM is incompatible with the firmware version on the fabric interconnect. | If you see this fault, take the following actions: - If the IOM and fabric interconnects are not running the same firmware version, wait for the auto-upgrade to complete. - When the IOM upgrade is completed, verify that Cisco UCS Manager has cleared this fault. - If you see this fault after the IOM overall status changes to operable, create a show tech-support file and contact Cisco TAC. | none | TRUE | connectivity | equipment:IOCard | sys/chassis-[id]/slot-[id] | 435 | fltEquipmentIOCardAutoUpgradingFirmware
F0436 | fltFirmwarePackItemImageMissing | [type] image with vendor [hwVendor], model [hwModel] and version [version] is deleted | major | image-deleted | This fault typically occurs when the image to which a firmware package item refers is missing. | If you see this fault, take the following actions: - In Cisco UCS Manager GUI, navigate to the Firmware Management Images tab and determine whether the missing image is available or not. - If the image is present, click on it to verify the model and vendor. - If the image for the required model and vendor is not present, download that image or bundle from the Cisco.com website. - If the image is present and the fault persists, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | firmware:PackItem | org-[name]/pack-image-[hwVendor]¦[hwModel]¦[type] | 436 | fltFirmwarePackItemImageMissing
F0440 | fltEtherSwitchIntFIoSatellite-wiring-numbers-unexpected | Chassis discovery policy conflict: Link IOM [chassisId]/[slotId]/[portId] to fabric interconnect [switchId]:[peerSlotId]/[peerPortId] not configured | info | unexpected-number-of-links | The configuration of the chassis discovery policy conflicts with the physical IOM uplinks. Cisco UCS Manager raises this fault when the chassis discovery policy is configured for more links than are physically cabled between the IOM uplinks on the chassis and the fabric interconnect. | If you see this fault, take the following actions: - Ensure that you cable at least the same number of IOM uplinks as are configured in the chassis discovery policy, and that you configure the corresponding server ports on the fabric interconnect. - Reacknowledge the chassis. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | connectivity | ether:SwitchIntFIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 440 | fltEtherSwitchIntFIoSatelliteWiringNumbersUnexpected
F0451 | fltMgmtEntityManagement-services-failure | Fabric Interconnect [id], management services have failed | critical | management-services-failure | This fault occurs in an unlikely event that management services fail on a fabric interconnect. This impacts the full HA functionality of the fabric interconnect cluster. | If you see this fault, take the following actions: - Verify that the initial setup configuration is correct on both fabric interconnects. - Verify that the L1 and L2 links are properly connected between the fabric interconnects. - Reboot the fabric interconnects. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | management | mgmt:Entity | sys/mgmt-entity-[id] | 451 | fltMgmtEntityManagementServicesFailure
F0452 | fltMgmtEntityManagement-services-unresponsive | Fabric Interconnect [id], management services are unresponsive | critical | management-services-unresponsive | This fault occurs when management services on a fabric interconnect are unresponsive. This impacts the full HA functionality of the fabric interconnect cluster. | If you see this fault, take the following actions: - Verify that the initial setup configuration is correct on both fabric interconnects. - Verify that the L1 and L2 links are properly connected between the fabric interconnects. - Reboot the fabric interconnects. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | management | mgmt:Entity | sys/mgmt-entity-[id] | 452 | fltMgmtEntityManagementServicesUnresponsive
F0456 | fltEquipmentChassisInoperable | Chassis [id] operability: [operability] | critical | equipment-inoperable | This fault typically occurs for one of the following reasons: - The fabric interconnect cannot communicate with a chassis. For a cluster configuration, this fault means that neither fabric interconnect can communicate with the chassis. - The chassis has an invalid FRU. | If you see this fault, take the following actions: - In Cisco UCS Manager, reacknowledge the chassis that raised the fault. - Physically unplug and replug the power cord into the chassis. - Verify that the I/O modules are functional. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Chassis | sys/chassis-[id] | 456 | fltEquipmentChassisInoperable
F0458 | fltEtherServerIntFIoHardware-failure | IOM [transport] interface [portId] on chassis [id] oper state: [operState], reason: [stateQual]Fabric Interconnect [transport] interface [portId] on fabric interconnect [id] oper state: [operState], reason: [stateQual]IOM [transport] interface [portId] on fex [id] oper state: [operState], reason: [stateQual] | major | interface-failed | This fault is raised on the IOM/FEX backplane ports when Cisco UCS Manager detects a hardware failure. | If you see this fault, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | ether:ServerIntFIo | sys/chassis-[id]/blade-[slotId]/diag/port-[portId] | 458 | fltEtherServerIntFIoHardwareFailure
F0459 | fltDcxVcMgmt-vif-down | IOM [chassisId] / [slotId] ([switchId]) management VIF [id] down, reason [stateQual] | major | cmc-vif-down | This fault occurs when the transport VIF for an I/O module is down. Cisco UCS Manager raises this fault when a fabric interconnect reports the connectivity state on virtual interface as one of the following: - Down - Errored - Unavailable | If you see this fault, take the following actions: - Verify that the chassis discovery has gone through successfully. Check the states on all communicating ports from end to end. - If connectivity seems correct, decommission and recommission the chassis. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | dcx:Vc | sys/chassis-[id]/blade-[slotId]/fabric-[switchId]/vc-[id] | 459 | fltDcxVcMgmtVifDown
F0460 | fltSysdebugMEpLogMEpLogLog | Log capacity on [side] IOM [chassisId]/[id] is [capacity]Log capacity on Management Controller on server [chassisId]/[slotId] is [capacity]Log capacity on Management Controller on server [id] is [capacity] | info | log-capacity | This fault typically occurs because Cisco UCS Manager has detected that the system event log (SEL) on the server is approaching full capacity. The available capacity in the log is low. This is an info-level fault and can be ignored if you do not want to clear the SEL at this time. | If you see this fault, you can clear the SEL in Cisco UCS Manager if desired. | none | TRUE | operational | sysdebug:MEpLog | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt/log-[type]-[id] | 460 | fltSysdebugMEpLogMEpLogLog
F0461 | fltSysdebugMEpLogMEpLogVeryLow | Log capacity on [side] IOM [chassisId]/[id] is [capacity]Log capacity on Management Controller on server [chassisId]/[slotId] is [capacity]Log capacity on Management Controller on server [id] is [capacity] | info | log-capacity | This fault typically occurs because Cisco UCS Manager has detected that the system event log (SEL) on the server is almost full. The available capacity in the log is very low. This is an info-level fault and can be ignored if you do not want to clear the SEL at this time. | If you see this fault, you can clear the SEL in Cisco UCS Manager if desired. | none | TRUE | operational | sysdebug:MEpLog | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt/log-[type]-[id] | 461 | fltSysdebugMEpLogMEpLogVeryLow
F0462 | fltSysdebugMEpLogMEpLogFull | Log capacity on [side] IOM [chassisId]/[id] is [capacity]Log capacity on Management Controller on server [chassisId]/[slotId] is [capacity]Log capacity on Management Controller on server [id] is [capacity] | info | log-capacity | This fault typically occurs because Cisco UCS Manager could not transfer the SEL file to the location specified in the SEL policy. This is an info-level fault and can be ignored if you do not want to clear the SEL at this time. | If you see this fault, take the following actions: - Verify the configuration of the SEL policy to ensure that the location, user, and password provided are correct. - If you do want to transfer and clear the SEL and the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | operational | sysdebug:MEpLog | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt/log-[type]-[id] | 462 | fltSysdebugMEpLogMEpLogFull
F0463 | fltComputePoolEmpty | server pool [name] is empty | minor | empty-pool | This fault typically occurs when the selected server pool does not contain any servers. | If you see this fault, take the following actions: - Verify the qualifier settings in the server pool policy qualifications. If the policy was modified after the server was discovered, reacknowledge the server. - Manually associate the service profile with a server. - If the server pool is not used, ignore the fault. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | compute:Pool | org-[name]/compute-pool-[name] | 463 | fltComputePoolEmpty
F0464 | fltUuidpoolPoolEmpty | UUID suffix pool [name] is empty | minor | empty-pool | This fault typically occurs when a UUID suffix pool does not contain any UUID suffixes. | If you see this fault, take the following actions: - If the pool is in use, add a block of UUID suffixes to the pool. - If the pool is not in use, ignore the fault. | none | TRUE | server | uuidpool:Pool | org-[name]/uuid-pool-[name] | 464 | fltUuidpoolPoolEmpty
F0465 | fltIppoolPoolEmpty | IP pool [name] is empty | minor | empty-pool | This fault typically occurs when an IP address pool does not contain any IP addresses. | If you see this fault, take the following actions: - If the pool is in use, add a block of IP addresses to the pool. - If the pool is not in use, ignore the fault. | none | TRUE | server | ippool:Pool | org-[name]/ip-pool-[name] | 465 | fltIppoolPoolEmpty
F0466 | fltMacpoolPoolEmpty | MAC pool [name] is empty | minor | empty-pool | This fault typically occurs when a MAC address pool does not contain any MAC addresses. | If you see this fault, take the following actions: - If the pool is in use, add a block of MAC addresses to the pool. - If the pool is not in use, ignore the fault. | none | TRUE | server | macpool:Pool | org-[name]/mac-pool-[name] | 466 | fltMacpoolPoolEmpty
F0470 | fltFirmwareUpdatableImageUnusable | backup image is unusable. reason: [operStateQual] | major | image-unusable | This fault typically occurs when the backup firmware image on an endpoint is unusable. | If you see this fault, take the following actions: - Review the fault and the error message on the FSM tab for the endpoint to determine why the firmware image is unusable. - If the firmware image is bad or corrupted, download another copy from the Cisco website and update the backup version on the endpoint with the new image. - If the image is present and the fault persists, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | firmware:Updatable | sys/chassis-[id]/blade-[slotId]/bios/fw-updatable | 470 | fltFirmwareUpdatableImageUnusable
F0471 | fltFirmwareBootUnitCantBoot | unable to boot the startup image. End point booted with backup image | major | image-cannot-boot | This fault typically occurs when the startup firmware image on an endpoint is corrupted or invalid, and the endpoint cannot boot from that image. | If you see this fault, take the following actions: - Review the fault and the error message on the FSM tab for the endpoint to determine why the firmware image is unusable. The error message usually includes an explanation for why the endpoint could not boot from the startup image, such as Bad-Image or Checksum Failed. - If the firmware image is bad or corrupted, download another copy from the Cisco website and update the startup version on the endpoint with the new image. - If the fault persists, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | firmware:BootUnit | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/fw-boot-def/bootunit-[type] | 471 | fltFirmwareBootUnitCantBoot
F0476 | fltFcpoolInitiatorsEmpty | FC pool [purpose] [name] is empty | minor | empty-pool | This fault typically occurs when a WWN pool does not contain any WWNs. | If you see this fault, take the following actions: - If the pool is in use, add a block of WWNs to the pool. - If the pool is not in use, ignore the fault. | none | TRUE | server | fcpool:Initiators | org-[name]/wwn-pool-[name] | 476 | fltFcpoolInitiatorsEmpty
F0478 | fltEquipmentIOCardInaccessible | [side] IOM [chassisId]/[id] ([switchId]) is inaccessible | critical | equipment-inaccessible | This fault typically occurs because an I/O module has lost its connection to the fabric interconnects. In a cluster configuration, the chassis fails over to the other I/O module. For a standalone configuration, the chassis associated with the I/O module loses network connectivity. This is a critical fault because it can result in the loss of network connectivity and disrupt data traffic through the I/O module. | If you see this fault, take the following actions: - Wait a few minutes to see if the fault clears. This is typically a temporary issue, and can occur after a firmware upgrade. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:IOCard | sys/chassis-[id]/slot-[id] | 478 | fltEquipmentIOCardInaccessible
F0479 | fltDcxVIfLinkState | Virtual interface [id] link state is down | major | vif-down | This fault occurs when Cisco UCS cannot send or receive data through an uplink port. | If you see this fault, take the following actions: - Reenable the uplink port that failed. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | dcx:VIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/ext-eth-[id]/vif-[id] | 479 | fltDcxVIfLinkState
F0480 | fltEquipmentFanModuleDegraded | Fan module [tray]-[id] in chassis [id] operability: [operability]Fan module [tray]-[id] in server [id] operability: [operability]Fan module [tray]-[id] in fabric interconnect [id] operability: [operability] | minor | equipment-degraded | This fault occurs when a fan module is not operational. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the fan module. - Review the Cisco UCS Site Preparation Guide to ensure the fan module has adequate airflow, including front and back clearance. - Verify that the air flows for the fan module are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:FanModule | sys/rack-unit-[id]/fan-module-[tray]-[id] | 480 | fltEquipmentFanModuleDegraded
F0481 | fltEquipmentIOCardPost-failure | [side] IOM [chassisId]/[id] ([switchId]) POST failure | major | equipment-problem | This fault typically occurs when an I/O module encounters errors during the Power On Self Test (POST). The impact of this fault varies according to the errors that were encountered during POST. | If you see this fault, take the following actions: - Check the POST results for the I/O module. In Cisco UCS Manager GUI, you can access the POST results from the General tab for the I/O module. In Cisco UCS Manager CLI, you can access the POST results through the show post command under the scope for the I/O module. - Reboot the I/O module. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:IOCard | sys/chassis-[id]/slot-[id] | 481 | fltEquipmentIOCardPostFailure
F0484 | fltEquipmentFanPerfThresholdLowerNonRecoverable | Fan [id] in Fan Module [tray]-[id] under chassis [id] speed: [perf]Fan [id] in fabric interconnect [id] speed: [perf]Fan [id] in Fan Module [tray]-[id] under server [id] speed: [perf] | critical | performance-problem | This fault occurs when the fan speed reading from the fan controller is far below the desired fan speed, and the fan has likely failed. | If you see this fault, create a detailed show tech-support file for the chassis and replace the fan module. If necessary, contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Fan | sys/rack-unit-[id]/fan-module-[tray]-[id]/fan-[id] | 484 | fltEquipmentFanPerfThresholdLowerNonRecoverable
F0502 | fltMemoryUnitIdentity-unestablishable | DIMM [location] on server [chassisId]/[slotId] has an invalid FRUDIMM [location] on server [id] has an invalid FRU | warning | identity-unestablishable | This fault typically occurs because Cisco UCS Manager has detected unsupported DIMM in the server. For example, the model, vendor, or revision is not recognized. | If you see this fault, take the following actions: - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, you may have unsupported DIMMs or DIMM configuration in the server. Create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | memory:Unit | sys/chassis-[id]/blade-[slotId]/board/memarray-[id]/mem-[id] | 502 | fltMemoryUnitIdentityUnestablishable
F0517 | fltComputePhysicalPost-failure | Server [id] POST or diagnostic failureServer [chassisId]/[slotId] POST or diagnostic failure | major | equipment-problem | This fault typically occurs when the server has encountered a diagnostic failure or an error during POST. | If you see this fault, take the following actions: - Check the POST results for the server. In Cisco UCS Manager GUI, you can access the POST results from the General tab for the server. In Cisco UCS Manager CLI, you can access the POST results through the show post command under the scope for the server. - Reboot the server. - If the above actions did not resolve the issue, execute the show tech-support command and contact Cisco Technical Support. | none | TRUE | server | compute:Physical |  | 517 | fltComputePhysicalPostFailure
F0528 | fltEquipmentPsuOffline | Power supply [id] in chassis [id] power: [power]Power supply [id] in fabric interconnect [id] power: [power]Power supply [id] in fex [id] power: [power]Power supply [id] in server [id] power: [power] | warning | equipment-offline | This fault typically occurs when Cisco UCS Manager detects that a power supply unit in a chassis, fabric interconnect, or FEX is offline. | If you see this fault, take the following actions: - Verify that the power cord is properly connected to the PSU and the power source. - Verify that the power source is 220 volts. - Verify that the PSU is properly installed in the chassis or fabric interconnect. - Remove the PSU and reinstall it. - Replace the PSU. - If the above actions did not resolve the issue, note down the type of PSU, execute the show tech-support command, and contact Cisco Technical Support. | environmental | TRUE | environmental | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 528 | fltEquipmentPsuOffline
F0531 | fltStorageRaidBatteryInoperable | RAID Battery on server [chassisId]/[slotId] operability: [operability]RAID Battery on server [id] operability: [operability] | major | equipment-inoperable | This fault occurs when the RAID battery voltage is below the normal operating range. | If you see this fault, take the following actions: - Replace the RAID battery. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | storage:RaidBattery | sys/chassis-[id]/blade-[slotId]/board/storage-[type]-[id]/raid-battery | 531 | fltStorageRaidBatteryInoperable
F0532 | fltSysdebugMEpLogTransferError | Server [chassisId]/[slotId] [type] transfer failed: [operState]Server [id] [type] transfer failed: [operState] | info | file-transfer-failed | This fault occurs when the transfer of a managed endpoint log file, such as the SEL, fails. | If you see this fault, take the following actions: - If the fault is related to the SEL, verify the connectivity to the CIMC on the server. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | operational | sysdebug:MEpLog | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt/log-[type]-[id] | 532 | fltSysdebugMEpLogTransferError
F0533 | fltComputeRtcBatteryInoperable | RTC Battery on server [chassisId]/[slotId] operability: [operability] | major | equipment-inoperable | This fault is raised when the CMOS battery voltage is below the normal operating range. This impacts the system clock. | If you see this fault, replace the CMOS battery. | diagnostic | TRUE | equipment | compute:RtcBattery | sys/chassis-[id]/blade-[slotId]/board/rtc-battery | 533 | fltComputeRtcBatteryInoperable
F0535 | fltMemoryBufferUnitThermalThresholdNonCritical | Buffer Unit [id] on server [chassisId]/[slotId] temperature: [thermal]Buffer Unit [id] on server [id] temperature: [thermal] | minor | thermal-problem | This fault occurs when the temperature of a memory buffer unit on a blade or rack server exceeds a non-critical threshold value, but is still below the critical threshold. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the server. - Review the Cisco UCS Site Preparation Guide to ensure the servers have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis or rack server are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | memory:BufferUnit | sys/chassis-[id]/blade-[slotId]/board/sensor-unit-[id] | 535 | fltMemoryBufferUnitThermalThresholdNonCritical
F0536 | fltMemoryBufferUnitThermalThresholdCritical | Buffer Unit [id] on server [chassisId]/[slotId] temperature: [thermal]Buffer Unit [id] on server [id] temperature: [thermal] | major | thermal-problem | This fault occurs when the temperature of a memory buffer unit on a blade or rack server exceeds a critical threshold value. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the server. - Review the Cisco UCS Site Preparation Guide to ensure the servers have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis or rack server are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | memory:BufferUnit | sys/chassis-[id]/blade-[slotId]/board/sensor-unit-[id] | 536 | fltMemoryBufferUnitThermalThresholdCritical
F0537 | fltMemoryBufferUnitThermalThresholdNonRecoverable | Buffer Unit [id] on server [chassisId]/[slotId] temperature: [thermal]Buffer Unit [id] on server [id] temperature: [thermal] | critical | thermal-problem | This fault occurs when the temperature of a memory buffer unit on a blade or rack server has been out of the operating range, and the issue is not recoverable. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the server. - Review the Cisco UCS Site Preparation Guide to ensure the servers have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis or rack server are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | memory:BufferUnit | sys/chassis-[id]/blade-[slotId]/board/sensor-unit-[id] | 537 | fltMemoryBufferUnitThermalThresholdNonRecoverable
F0538 | fltComputeIOHubThermalNonCritical | IO Hub on server [chassisId]/[slotId] temperature: [thermal] | minor | thermal-problem | This fault is raised when the IO controller temperature is outside the upper or lower non-critical threshold. | If you see this fault, monitor other environmental events related to this server and ensure the temperature ranges are within recommended ranges. | environmental | TRUE | environmental | compute:IOHub | sys/chassis-[id]/blade-[slotId]/board/iohub | 538 | fltComputeIOHubThermalNonCritical
F0539 | fltComputeIOHubThermalThresholdCritical | IO Hub on server [chassisId]/[slotId] temperature: [thermal] | major | thermal-problem | This fault is raised when the IO controller temperature is outside the upper or lower critical threshold. | If you see this fault, take the following actions: - Monitor other environmental events related to the server and ensure the temperature ranges are within recommended ranges. - Consider turning off the server for a while if possible. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | compute:IOHub | sys/chassis-[id]/blade-[slotId]/board/iohub | 539 | fltComputeIOHubThermalThresholdCritical
F0540 | fltComputeIOHubThermalThresholdNonRecoverable | IO Hub on server [chassisId]/[slotId] temperature: [thermal] | critical | thermal-problem | This fault is raised when the IO controller temperature is outside the recoverable range of operation. | If you see this fault, take the following actions: - Shutdown the server immediately. - Create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | compute:IOHub | sys/chassis-[id]/blade-[slotId]/board/iohub | 540 | fltComputeIOHubThermalThresholdNonRecoverable
F0543 | fltEquipmentChassisIdentity-unestablishable | Chassis [id] has an invalid FRU | major | identity-unestablishable | This fault typically occurs because Cisco UCS Manager has detected an unsupported chassis. For example, the model, vendor, or revision is not recognized. | If you see this fault, take the following actions: - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, execute the show tech-support command and contact Cisco technical support. | none | TRUE | equipment | equipment:Chassis | sys/chassis-[id] | 543 | fltEquipmentChassisIdentityUnestablishable
F0549 | fltSwVlanPortNsResourceStatus | Vlan-Port Resource exceeded | critical | limit-reached | This fault occurs when the total number of configured VLANs in the Cisco UCS instance has exceeded the allowed maximum number of configured VLANs on the fabric interconnect. | If you see this fault, take the following actions: - In the Cisco UCS Manager CLI or Cisco UCS Manager GUI, check the port VLAN count to determine by how many VLANs the system is over the maximum. - Reduce the VLAN port count in one of the following ways: - Delete VLANs configured on the LAN cloud. - Delete VLANs configured on vNICs. - Unconfigure one or more vNICs. - Unconfigure one or more uplink Ethernet ports on the fabric interconnect. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | management | sw:VlanPortNs | sys/switch-[id]/vlan-port-ns | 549 | fltSwVlanPortNsResourceStatus
F0620 | fltFabricVlanPrimaryVlanMissingIsolated | Primary Vlan can not be resolved for isolated vlan [name] | minor | primary-vlan-missing-isolated | This fault typically occurs when Cisco UCS Manager encounters a problem resolving the primary VLAN ID corresponding to a particular isolated VLAN. | If you see this fault, take the following actions: - Associate the isolated VLAN with a valid primary VLAN. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:Vlan | fabric/eth-estc/[id]/net-[name] | 620 | fltFabricVlanPrimaryVlanMissingIsolated
F0621 | fltFabricLanPinGroupEmpty | LAN Pin Group [name] is empty | minor | empty-pin-group | This fault typically occurs when a LAN pin group does not contain any targets. | If you see this fault, add a target to the LAN pin group. | none | TRUE | server | fabric:LanPinGroup | fabric/lan/lan-pin-group-[name] | 621 | fltFabricLanPinGroupEmpty
F0622 | fltFabricSanPinGroupEmpty | SAN Pin Group [name] is empty | minor | empty-pin-group | This fault typically occurs when a SAN pin group does not contain any targets. | If you see this fault, add a target to the SAN pin group. | none | TRUE | server | fabric:SanPinGroup | fabric/san/san-pin-group-[name] | 622 | fltFabricSanPinGroupEmpty
F0625 | fltAdaptorExtEthIfMisConnect | Adapter [id] eth interface [id] in server [id] mis-connected | warning | link-misconnected | The link for a network-facing adapter interface is misconnected. Cisco UCS Manager raises this fault when any of the following scenarios occur: - Cisco UCS Manager detects a new connectivity between a previously configured switch port or FEX port and the adapter's external interface. - Cisco UCS Manager detects a misconnected link between a fabric interconnect or FEX and its non-peer adapter's interface. | If you see this fault, take the following actions: - Check whether the adapter link is connected to a port that belongs to its peer fabric interconnect or FEX. - If that connectivity seems correct, reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | adaptor:ExtEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/ext-eth-[id] | 625 | fltAdaptorExtEthIfMisConnect
F0626 | fltAdaptorHostEthIfMisConnect | Adapter [id] eth interface [id] in server [id] mis-connected | warning | link-misconnected | The link for a network-facing host interface is misconnected. Cisco UCS Manager raises this fault when any of the following scenarios occur: - Cisco UCS Manager detects a new connectivity between a previously configured switch port and the host Ethernet interface. - Cisco UCS Manager detects a misconnected link between the host interface and its non-peer fabric interconnect. | If you see this fault, take the following actions: - Check whether the host Ethernet interface is connected to a port belonging to its peer fabric interconnect. - If connectivity seems correct, reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 626 | fltAdaptorHostEthIfMisConnect
F0635 | fltPowerBudgetPowerBudgetCmcProblem | Power cap application failed for chassis [id] | major | power-cap-fail | This fault typically occurs when the server CIMC has failed to enforce the configured power cap. | If you see this fault, take the following actions: - Check the power consumption of the chassis. If the chassis is consuming significantly more power than configured in the power cap, consider reducing the group cap so that the power consumption of other chassis consumption can be reduced to make up for the increase. - If the above action did not resolve the issue, create a show tech-support file for Cisco UCS Manager and the chassis and then contact Cisco TAC. | none | TRUE | environmental | power:Budget | sys/chassis-[id]/blade-[slotId]/budget | 635 | fltPowerBudgetPowerBudgetCmcProblem
F0637 | fltPowerBudgetPowerBudgetBmcProblem | Power cap application failed for server [chassisId]/[slotId]Power cap application failed for server [id] | major | power-cap-fail | This fault typically occurs when the server CIMC or BIOS has failed to enforce the configured power cap. | If you see this fault, take the following actions: - Check the power consumption of the blade server. If the server is consuming significantly more power than configured in the power cap, switch to a manual per blade cap configuration. If the power consumption is still too high, consider reducing the group cap so that the power consumption of other chassis consumption can be reduced to make up for the increase. - If the power consumption is still too high, the CIMC or BIOS software is likely faulty. - Create a show tech-support file for Cisco UCS Manager and the chassis and then contact Cisco TAC. | none | TRUE | environmental | power:Budget | sys/chassis-[id]/blade-[slotId]/budget | 637 | fltPowerBudgetPowerBudgetBmcProblem
F0640 | fltPowerBudgetPowerBudgetDiscFail | Insufficient power available to discover server [chassisId]/[slotId]Insufficient power available to discover server [id] | major | power-cap-fail | This fault typically occurs when discovery fails due to unavailable power in the group. | If you see this fault, take the following actions: - Consider increasing the group cap. - Reduce the number of blade servers or chassis in the Cisco UCS instance. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | power:Budget | sys/chassis-[id]/blade-[slotId]/budget | 640 | fltPowerBudgetPowerBudgetDiscFail
F0642 | fltPowerGroupPowerGroupInsufficientBudget | insufficient budget for power group [name] | major | power-cap-fail | This fault typically occurs when the group cap is insufficient to meet the minimum hardware requirements. | If you see this fault, take the following actions: - Consider increasing the group cap. - Reduce the number of blade servers or chassis in the Cisco UCS instance. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | power:Group | sys/power-ep/group-[name] | 642 | fltPowerGroupPowerGroupInsufficientBudget
F0643 | fltPowerGroupPowerGroupBudgetIncorrect | admin committed insufficient for power group [name], using previous value [operCommitted] | major | power-cap-fail | This fault typically occurs when the group cap is insufficient to meet the minimum hardware requirements. Under these circumstances, Cisco UCS Manager uses the previously entered group cap for provisioning. | If you see this fault, take the following actions: - Consider increasing the group cap. - Reduce the number of blade servers or chassis in the Cisco UCS instance. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | power:Group | sys/power-ep/group-[name] | 643 | fltPowerGroupPowerGroupBudgetIncorrect
F0670 | fltLicenseInstanceGracePeriodWarning1 | license for [feature] on fabric-interconnect [scope] has entered into the grace period. | warning | license-graceperiod-entered | At least one port on the fabric interconnect is running in the grace period. This fault typically occurs if one or more ports on the fixed module are enabled after all default licenses have been assigned to a port. | If you see this fault, take the following actions: - Check the number of licenses installed and being used on each fabric interconnect. In the Cisco UCS Manager GUI, you can access the licensing information from the Admin tab for the fabric interconnect. In the Cisco UCS Manager CLI, you can access the licensing information by entering the show usage detail command under the license scope. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 670 | fltLicenseInstanceGracePeriodWarning1
F0671 | fltLicenseInstanceGracePeriodWarning2 | license for [feature] on fabric-interconnect [scope] is running in the grace period for more than 10 days | warning | license-graceperiod-10days | At least one port on the fabric interconnect has been running in the grace period for more than 10 days. This fault typically occurs if one or more ports on the fixed module are enabled after all default licenses have been assigned to ports and the unlicensed ports have been running for more than 10 days. | If you see this fault, take the following actions: - Check the number of licenses installed and consumed on each fabric interconnect. In the Cisco UCS Manager GUI, you can access the licensing information from the Admin tab for the fabric interconnect. In the Cisco UCS Manager CLI, you can access the licensing information by entering the show usage detail command under the license scope. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 671 | fltLicenseInstanceGracePeriodWarning2
F0672 | fltLicenseInstanceGracePeriodWarning3 | license for [feature] on fabric-interconnect [scope] is running in the grace period for more than 30 days | warning | license-graceperiod-30days | At least one port on the fabric interconnect has been running in the grace period for more than 30 days. This fault typically occurs if one or more ports on the fixed module are enabled after all default licenses have been assigned to ports and the unlicensed ports have been running for more than 30 days. | If you see this fault, take the following actions: - Check the number of licenses installed and consumed on each fabric interconnect. In the Cisco UCS Manager GUI, you can access the licensing information from the Admin tab for the fabric interconnect. In the Cisco UCS Manager CLI, you can access the licensing information by entering the show usage detail command under the license scope. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 672 | fltLicenseInstanceGracePeriodWarning3
F0673 | fltLicenseInstanceGracePeriodWarning4 | license for [feature] on fabric-interconnect [scope] is running in the grace period for more than 60 days | warning | license-graceperiod-60days | At least one port on the fabric interconnect has been running in the grace period for more than 60 days. This fault typically occurs if one or more ports on the fixed module are enabled after all default licenses have been assigned to ports and the unlicensed ports have been running for more than 60 days. | If you see this fault, take the following actions: - Check the number of licenses installed and consumed on each fabric interconnect. In the Cisco UCS Manager GUI, you can access the licensing information from the Admin tab for the fabric interconnect. In the Cisco UCS Manager CLI, you can access the licensing information by entering the show usage detail command under the license scope. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 673 | fltLicenseInstanceGracePeriodWarning4
F0674 | fltLicenseInstanceGracePeriodWarning5 | license for [feature] on fabric-interconnect [scope] is running in the grace period for more than 90 days | major | license-graceperiod-90days | At least one port on the fabric interconnect has been running in the grace period for more than 90 days. This fault typically occurs if one or more ports on the fixed module are enabled after all default licenses have been assigned to ports and the unlicensed ports have been running for more than 90 days. | If you see this fault, take the following actions: - Check the number of licenses installed and consumed on each fabric interconnect. In the Cisco UCS Manager GUI, you can access the licensing information from the Admin tab for the fabric interconnect. In the Cisco UCS Manager CLI, you can access the licensing information by entering the show usage detail command under the license scope. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 674 | fltLicenseInstanceGracePeriodWarning5
F0675 | fltLicenseInstanceGracePeriodWarning6 | license for [feature] on fabric-interconnect [scope] is running in the grace period for more than 119 days | critical | license-graceperiod-119days | At least one port on the fabric interconnect has been running in the grace period for more than 119 days. This fault typically occurs if one or more ports on the fixed module are enabled after all default licenses have been assigned to ports and the unlicensed ports have been running for more than 119 days. | If you see this fault, take the following actions: - Check the number of licenses installed and consumed on each fabric interconnect. In the Cisco UCS Manager GUI, you can access the licensing information from the Admin tab for the fabric interconnect. In the Cisco UCS Manager CLI, you can access the licensing information by entering the show usage detail command under the license scope. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 675 | fltLicenseInstanceGracePeriodWarning6
F0676 | fltLicenseInstanceGracePeriodWarning7 | Grace period for [feature] on fabric-interconnect [scope] is expired. Please acquire a license for the same. | critical | license-graceperiod-expired | At least one port on the fabric interconnect has been running in the grace period for more than 120 days. This fault typically occurs if one or more ports on the fixed module are enabled after all default licenses have been assigned to ports and the unlicensed ports have been running for more than 120 days. At this stage, the system licensing state is set to expired. | If you see this fault, take the following actions: - Check the number of licenses installed and consumed on each fabric interconnect. In the Cisco UCS Manager GUI, you can access the licensing information from the Admin tab for the fabric interconnect. In the Cisco UCS Manager CLI, you can access the licensing information by entering the show usage detail command under the license scope. - Disable the unlicensed ports to bring the number of enabled ports down to the number of total licenses. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC immediately to procure more licenses. | environmental | TRUE | management | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 676 | fltLicenseInstanceGracePeriodWarning7
F0677 | fltLicenseFileBadLicenseFile | license file [name] on fabric-interconnect [scope] can not be installed | critical | license-file-uninstallable | The installation of a license file on the fabric interconnect failed. This fault typically occurs if the license file is badly formatted or its host ID does not match that of the fabric interconnect. | If you see this fault, take the following actions: - In the Cisco UCS Manager CLI, check the host IDs for both fabric interconnects. You can access the host ID information by entering the show server-host-id detail command under the license scope. - Match the host IDs with the contents of the license file. If the host ID matches that of one of the fabric interconnects, create a show tech-support file and contact Cisco TAC. If it does not match, contact Cisco TAC to obtain the correct license File. | none | FALSE | management | license:File | sys/license/file-[scope]:[id] | 677 | fltLicenseFileBadLicenseFile
F0678 | fltLicenseFileFileNotDeleted | license file [name] from fabric-interconnect [scope] could not be deleted | critical | license-file-not-deleted | The deletion of a license file on the fabric interconnect has failed. This fault typically occurs if license framework is not able to delete a file. | If you see this fault, create a show tech-support file and contact Cisco TAC. | none | FALSE | management | license:File | sys/license/file-[scope]:[id] | 678 | fltLicenseFileFileNotDeleted
F0688 | fltMgmtIfMisConnect | Management Port [id] in server [id] is mis connected | warning | link-misconnected | This fault occurs when the server and FEX connectivity changes. | If you see this fault, take the following actions: - Check the connectivity between the server and FEX. - If the connectivity was changed by mistake, restore it to its previous configuration. - If the connectivity change was intentional, reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | operational | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 688 | fltMgmtIfMisConnect
F0689 | fltLsComputeBindingAssignmentRequirementsNotMet | Assignment of service profile [name] to server [pnDn] failed | minor | assignment-failed | The server could not be assigned to the selected service profile. This fault typically occurs as a result of one of the following issues: - The selected server does not meet the requirements of the service profile. - If the service profile was configured for restricted migration, the selected server does not match the currently or previously assigned server. | If you see this fault, select a different server that meets the requirements of the service profile or matches the currently or previously assigned server. | none | TRUE | server | ls:ComputeBinding | org-[name]/tier-[name]/ls-[name]/ | 689 | fltLsComputeBindingAssignmentRequirementsNotMet
F0702 | fltEquipmentFexPost-failure | fex [id] POST failure | major | equipment-problem | This fault typically occurs when a FEX encounters errors during the Power On Self Test (POST). The impact of this fault varies depending on which errors were encountered during POST. | If you see this fault, take the following actions: - Check the POST results for the FEX. In the Cisco UCS Manager GUI, you can access the POST results from the General tab for the FEX. In the Cisco UCS Manager CLI, you can access the POST results by entering the show post command under the scope for the FEX. - Reboot the FEX. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Fex | sys/fex-[id] | 702 | fltEquipmentFexPostFailure
F0703 | fltEquipmentFexIdentity | Fex [id] has a malformed FRU | critical | fru-problem | This fault typically occurs when the FRU information for a FEX is corrupted or malformed. | If you see this fault, take the following actions: - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Fex | sys/fex-[id] | 703 | fltEquipmentFexIdentity
F0708 | fltAdaptorHostEthIfMissing | Connection to Adapter [id] eth interface [id] in server [id] missing | warning | link-missing | The link for a network-facing host interface is missing. Cisco UCS Manager raises this fault when it detects missing connectivity between a previously configured switch port and its previous peer host interface. | If you see this fault, take the following actions: - Check whether the adapter link is connected to a port that belongs to its non-peer fabric interconnect. - If that connectivity seems correct, reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 708 | fltAdaptorHostEthIfMissing
F0713 | fltPortPIoInvalid-sfp | [transport] port [portId] on chassis [id] role : [ifRole] transceiver type:[xcvrType][transport] port [portId] on fabric interconnect [id] role : [ifRole] transceiver type:[xcvrType] | major | unsupported-transceiver | This fault is raised against a fabric interconnect port, network-facing IOM port, or FEX module port if an unsupported transceiver type is inserted. The port cannot be used if it has an unsupported transceiver. | If you see this fault, replace the transceiver with a supported SFP type. Refer to the documentation on the Cisco website for a list of supported SFPs. | none | TRUE | network | port:PIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 713 | fltPortPIoInvalidSfp
F0717 | fltMgmtIfMissing | Connection to Management Port [id] in server [id] is missing | warning | link-missing | This fault occurs when the connectivity between a server and FEX is removed or unconfigured. | If you see this fault, take the following actions: - Check the connectivity between the server and FEX. - If the connectivity was changed by mistake, restore it to its previous configuration. - If the connectivity change was intentional, reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | operational | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 717 | fltMgmtIfMissing
F0727 | fltFabricEthLanPcEpDown | [type] Member [slotId]/[portId] of Port-Channel [portId] on fabric interconnect [id] is down, membership: [membership] | major | membership-down | This fault typically occurs when a member port in an Ethernet port channel is down. | If you see this fault, take the following action: - Check the link connectivity on the upstream Ethernet switch. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:EthLanPcEp | fabric/lan/[id]/pc-[portId]/ep-slot-[slotId]-port-[portId] | 727 | fltFabricEthLanPcEpDown
F0728 | fltFabricFcSanPcEpDown | [type] Member [slotId]/[portId] of Port-Channel [portId] on fabric interconnect [id] is down, membership: [membership] | major | membership-down | This fault typically occurs when a member port in a Fibre Channel port channel is down. | If you see this fault, take the following action: - Check the link connectivity on the upstream Fibre Channel switch - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:FcSanPcEp | fabric/san/[id]/pc-[portId]/ep-slot-[slotId]-port-[portId] | 728 | fltFabricFcSanPcEpDown
F0729 | fltEquipmentIOCardThermalThresholdNonCritical | [side] IOM [chassisId]/[id] ([switchId]) temperature: [thermal] | minor | thermal-problem | This fault occurs when the temperature of an I/O module has exceeded a non-critical threshold value, but is still below the critical threshold. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the I/O module. - Review the Cisco UCS Site Preparation Guide to ensure the chassis and I/O modules have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis and I/O module are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:IOCard | sys/chassis-[id]/slot-[id] | 729 | fltEquipmentIOCardThermalThresholdNonCritical
F0730 | fltEquipmentIOCardThermalThresholdCritical | [side] IOM [chassisId]/[id] ([switchId]) temperature: [thermal] | major | thermal-problem | This fault occurs when the temperature of an I/O module has exceeded a critical threshold value. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the I/O module. - Review the Cisco UCS Site Preparation Guide to ensure the chassis and I/O modules have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis and I/O module are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Replace the faulty I/O modules. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:IOCard | sys/chassis-[id]/slot-[id] | 730 | fltEquipmentIOCardThermalThresholdCritical
F0731 | fltEquipmentIOCardThermalThresholdNonRecoverable | [side] IOM [chassisId]/[id] ([switchId]) temperature: [thermal] | critical | thermal-problem | This fault occurs when the temperature of an I/O module has been out of the operating range, and the issue is not recoverable. Be aware of the following possible contributing factors: - Temperature extremes can cause Cisco UCS equipment to operate at reduced efficiency and cause a variety of problems, including early degradation, failure of chips, and failure of equipment. In addition, extreme temperature fluctuations can cause CPUs to become loose in their sockets. - Cisco UCS equipment should operate in an environment that provides an inlet air temperature not colder than 50F (10C) nor hotter than 95F (35C). - If sensors on a CPU reach 179.6F (82C), the system will take that CPU offline. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the I/O module. - Review the Cisco UCS Site Preparation Guide to ensure the chassis and I/O modules have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis and I/O module are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Clean the installation site at regular intervals to avoid buildup of dust and debris, which can cause a system to overheat. - Replace the faulty I/O modules. - Use the Cisco UCS power capping capability to limit power usage. Power capping can limit the power consumption of the system, including blade and rack servers, to a threshold that is less than or equal to the system's maximum rated power. Power-capping can have an impact on heat dissipation and help to lower the installation site temperature. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:IOCard | sys/chassis-[id]/slot-[id] | 731 | fltEquipmentIOCardThermalThresholdNonRecoverable
F0733 | fltEquipmentChassisSeeprom-inoperable | Device [id] SEEPROM operability: [seepromOperState] | critical | equipment-inoperable | This fault occurs in the unlikely event that the Chassis shared storage (SEEPROM) is not operational. | If you see this fault, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | equipment:Chassis | sys/chassis-[id] | 733 | fltEquipmentChassisSeepromInoperable
F0734 | fltFabricFcSanPcEpIncompatibleSpeed | Member [slotId]/[portId] cannot be added to SAN Port-Channel [portId] on fabric interconnect [id], reason: [membership] | major | incompatible-speed | This fault typically occurs when the maximum supported Fibre Channel speed of a port in a Fibre Channel port channel is incompatible with the admin speed configured for the port channel. | If you see this fault, take one of the following actions: - Change the admin speed of the port channel to match the maximum supported speed of the member ports in the port channel. - Replace the expansion module in the fabric interconnect with one that matches the admin speed configured for the port channel. | none | TRUE | network | fabric:FcSanPcEp | fabric/san/[id]/pc-[portId]/ep-slot-[slotId]-port-[portId] | 734 | fltFabricFcSanPcEpIncompatibleSpeed
F0735 | fltFabricFcSanPcIncompatibleSpeed | Cannot set admin speed to the requested value, Speed incompatible with member ports in the port-channel | major | incompatible-speed | This fault typically occurs when the maximum supported Fibre Channel speed of a port in a Fibre Channel port channel is incompatible with the admin speed configured for the port channel. | If you see this fault, take one of the following actions: - Change the admin speed of the port channel to match the maximum supported speed of the member ports in the port channel. - Replace the expansion module in the fabric interconnect with one that matches the admin speed configured for the port channel. | none | TRUE | network | fabric:FcSanPc | fabric/san/[id]/pc-[portId] | 735 | fltFabricFcSanPcIncompatibleSpeed
F0736 | fltExtmgmtIfMgmtifdown | Management interface on Fabric Interconnect [id] is [operState] | major | mgmtif-down | This fault occurs when a fabric interconnect reports that the operational state of an external management interface is down. | If you see this fault, take the following actions: - Check the state transitions of the external management interface on the fabric interconnect. - Check the link connectivity for the external management interface. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | management | extmgmt:If | sys/switch-[id]/extmgmt-intf | 736 | fltExtmgmtIfMgmtifdown
F0740 | fltPowerChassisMemberPowerGroupCapInsufficient | Chassis [id] cannot be capped as group cap is low. Please consider raising the cap. | major | group-cap-insufficient | This fault typically occurs when an updated group cap is insufficient to meet the minimum hardware requirements and a chassis that has just been added to the power group cannot be capped as a result. | If you see this fault, take the following actions: - Consider increasing the group cap. - Reduce the number of blade servers or chassis in the Cisco UCS instance. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | power:ChassisMember | sys/power-ep/group-[name]/ch-member-[id] | 740 | fltPowerChassisMemberPowerGroupCapInsufficient
F0741 | fltPowerChassisMemberChassisFirmwareProblem | Chassis [id] cannot be capped as at least one of the CMC or CIMC or BIOS firmware version is less than 1.4. Please upgrade the firmware for cap to be applied. | major | old-chassis-component-firmware | This fault typically occurs when the CIMC firmware on a server is an earlier release than Cisco UCS, Release 1.4. | If you see this fault, consider upgrading the CIMC firmware, and the entire Cisco UCS instance if necessary, to Cisco UCS, Release 1.4 or later. | none | TRUE | environmental | power:ChassisMember | sys/power-ep/group-[name]/ch-member-[id] | 741 | fltPowerChassisMemberChassisFirmwareProblem
F0742 | fltPowerChassisMemberChassisPsuInsufficient | Chassis [id] cannot be capped as at least two PSU need to be powered | major | psu-insufficient | This fault typically occurs when at least two PSUs are not powered on. | If you see this fault, insert at least two PSUs and power them on. | none | TRUE | environmental | power:ChassisMember | sys/power-ep/group-[name]/ch-member-[id] | 742 | fltPowerChassisMemberChassisPsuInsufficient
F0743 | fltPowerChassisMemberChassisPsuRedundanceFailure | Chassis [id] was configured for redundancy, but running in a non-redundant configuration. | major | psu-redundancy-fail | This fault typically occurs when chassis power redundancy has failed. | If you see this fault, take the following actions: - Consider adding more PSUs to the chassis. - Replace any non-functional PSUs. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | power:ChassisMember | sys/power-ep/group-[name]/ch-member-[id] | 743 | fltPowerChassisMemberChassisPsuRedundanceFailure
F0744 | fltPowerBudgetPowerCapReachedCommit | P-State lowered as consumption hit power cap for server [chassisId]/[slotId]P-State lowered as consumption hit power cap for server [id] | info | power-consumption-hit-limit | This fault typically occurs when Cisco UCS Manager is actively capping the power for a blade server. | If you see this fault, no action is needed. | none | TRUE | environmental | power:Budget | sys/chassis-[id]/blade-[slotId]/budget | 744 | fltPowerBudgetPowerCapReachedCommit
F0747 | fltSysdebugAutoCoreFileExportTargetAutoCoreTransferFailure | Auto core transfer failure at remote server [hostname]:[path] [exportFailureReason] | warning | tftp-server-error | This fault occurs when Cisco UCS Manager cannot transfer a core file to a remote TFTP server. This is typically the result of one of the following issues: - The remote TFTP server is not accessible. - One or more of the parameters for the TFTP server that are specified for the core export target, such as path, port, and server name, are incorrect. | If you see this fault, take the following actions: - Verify the connectivity to the remote server. - Verify the path information of the remote server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | sysdebug | sysdebug:AutoCoreFileExportTarget | sys/sysdebug/file-export | 747 | fltSysdebugAutoCoreFileExportTargetAutoCoreTransferFailure
F0757 | fltFabricMonSpanConfigFail | Configuration for traffic monitor [name] failed, reason: [configFailReason] | major | config-error | This fault typically occurs when the configuration of a traffic monitoring session is incorrect. | If you see this fault, correct the configuration problem provided in the fault description. | none | TRUE | network | fabric:Mon |  | 757 | fltFabricMonSpanConfigFail
F0764 | fltPowerBudgetChassisPsuInsufficient | Chassis [id] has had PSU failures. Please correct the problem by checking input power or replace the PSU | major | psu-failure | This fault typically occurs when at least two PSUs are not powered on. | If you see this fault, insert at least two PSUs and power them on. | none | TRUE | environmental | power:Budget | sys/chassis-[id]/blade-[slotId]/budget | 764 | fltPowerBudgetChassisPsuInsufficient
F0765 | fltPowerBudgetTStateTransition | Blade [chassisId]/[slotId] has been severely throttled. CIMC can recover if budget is redeployed to the blade or by rebooting the blade. If problem persists, please ensure that OS is ACPI compliantRack server [id] has been severely throttled. CIMC can recover if budget is redeployed to the blade or by rebooting the blade. If problem persists, please ensure that OS is ACPI compliant | critical | no-ack-from-bios | This fault typically occurs when the processor T-state is used to severely throttle the CPU. | If you see this fault, take the following actions: - Redeploy the power budget for the affected power group, blade server, or chassis. - If the problem persists, reboot the blade server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | power:Budget | sys/chassis-[id]/blade-[slotId]/budget | 765 | fltPowerBudgetTStateTransition
F0766 | fltPowerPolicyPowerPolicyApplicationFail | Insufficient budget to apply no-cap priority through policy [name]. Blades will continue to be capped | minor | no-cap-fail | This fault occurs when a power policy cannot be applied to one or more blade servers. The affected blade servers cannot operate normally without power capping due to the limited power budget for those servers. | If you see this fault, take the following actions: - Increase the power budget for the blade servers in the power policy. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | power:Policy | org-[name]/power-policy-[name] | 766 | fltPowerPolicyPowerPolicyApplicationFail
F0772 | fltMgmtIfNew | New connection discovered on Management Port [id] in server [id] | warning | new-link | This fault occurs when the connectivity between a server and a FEX is added or changed. | If you see this fault, take the following actions: - Check the connectivity between the server and FEX. - If the connectivity was changed by mistake, restore it to its previous configuration. - If the connectivity change was intentional, reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | operational | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 772 | fltMgmtIfNew
F0775 | fltAdaptorExtEthIfMissing | Connection to Adapter [id] eth interface [id] in server [id] missing | warning | link-missing | The link for a network-facing adapter interface is misconnected. Cisco UCS Manager raises this fault when it detects that the connectivity between a previously configured port on a fabric interconnect or FEX and its prior peer network-facing adapter interface is misconnected or missing. | If you see this fault, take the following actions: - Check whether the adapter interface is connected to a port belonging to its peer fabric interconnect or FEX. - If the connectivity seems correct, reacknowledge the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | adaptor:ExtEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/ext-eth-[id] | 775 | fltAdaptorExtEthIfMissing
F0776 | fltStorageLocalDiskSlotEpUnusable | Local disk [id] on server [serverId] is not usable by the operating system | minor | equipment-inoperable | This fault occurs when the server disk drive is in a slot that is not supported by the storage controller. | If you see this fault, take the following actions: - Insert the server disk drive in a supported slot. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | storage:LocalDiskSlotEp | sys/chassis-[id]/blade-[slotId]/board/disk-[id] | 776 | fltStorageLocalDiskSlotEpUnusable
F0777 | fltFabricEthEstcPcEpDown | [type] Member [slotId]/[portId] of Port-Channel [portId] on fabric interconnect [id] is down, membership: [membership] | major | membership-down | This fault typically occurs when a member port in an Ethernet port channel is down. | If you see this fault, take the following action: - Check the link connectivity on the upstream Ethernet switch. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:EthEstcPcEp | fabric/eth-estc/[id]/pc-[portId]/ep-slot-[slotId]-port-[portId] | 777 | fltFabricEthEstcPcEpDown
F0778 | fltEquipmentFexIdentity-unestablishable | Fex [id] has an invalid FRU | major | identity-unestablishable | This fault typically occurs because Cisco UCS Manager detected an unsupported chassis. For example, the model, vendor, or revision is not recognized. | If you see this fault, take the following actions: - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:Fex | sys/fex-[id] | 778 | fltEquipmentFexIdentityUnestablishable
F0794 | fltEquipmentFanModuleInoperable | Fan module [tray]-[id] in chassis [id] operability: [operability]Fan module [tray]-[id] in server [id] operability: [operability]Fan module [tray]-[id] in fabric interconnect [id] operability: [operability] | major | equipment-inoperable | This fault occurs if a fan module is not operational. | If you see this fault, take the following actions: - Remove and reinstall the fan module. If multiple fans are affected by this fault, remove and reinstall one fan module at a time. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | equipment | equipment:FanModule | sys/rack-unit-[id]/fan-module-[tray]-[id] | 794 | fltEquipmentFanModuleInoperable
F0795 | fltLsmaintMaintPolicyUnresolvableScheduler | Schedule [schedName] referenced by maintenance policy [name] does not exist | warning | non-existent-scheduler | The schedule that is referenced by the maintenance policy does not exist. This fault typically occurs as a result of one of the following issues: - The schedule does not exist. - The schedule was deleted. | If you see this fault, take the following actions: - Check if the named schedule exists. If it is deleted or missing, try to create it. - If the named schedule is deleted or missing, recreate it. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | lsmaint:MaintPolicy | org-[name]/maint-[name] | 795 | fltLsmaintMaintPolicyUnresolvableScheduler
F0796 | fltFabricVsanErrorDisabled | VSAN [name] is [operState] | major | vsan-misconfigured | This fault typically occurs when the VSAN has an ID in the restricted range between 3840 and 4078, and Fibre Channel end host mode is enabled on the fabric interconnect. | If you see this fault, take the following actions: - Delete the port channels on the fabric interconnect. - Disable uplink trunking on the fabric-interconnect. - Configure the fabric interconnect for fibre channel switch mode. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:Vsan | fabric/fc-estc/[id]/net-[name] | 796 | fltFabricVsanErrorDisabled
F0797 | fltFabricVsanEpErrorDisabled | [type] Port [slotId]/[portId] on fabric interconnect [switchId] has VSAN [id] in error disabled statePort channel [portId] on fabric interconnect [switchId] has VSAN [id] in error disabled state | major | vsan-misconfigured | This fault typically occurs when a port is assigned to a VSAN that has an ID in the restricted range between 3840 and 4078) or is VSAN 4079, which is reserved. | If you see this fault, take the following action: - If the VSAN ID is in the restricted range between 3840 and 4078, do the following: - Delete the port channels on the fabric interconnect. - Disable uplink trunking on the fabric-interconnect. - Configure the fabric interconnect for fibre channel switch mode. - If the VSAN is VSAN 4079, which is reserved, assign the port to a non-reserved VSAN. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:VsanEp | fabric/fc-estc/[id]/phys-fc-slot-[slotId]-port-[portId]/vsan-[id] | 797 | fltFabricVsanEpErrorDisabled
F0798 | fltPowerBudgetFirmwareMismatch | Firmware on blade [chassisId]/[slotId] does not allow chassis level power capping. Please consider upgrading to at least 1.4 version | major | old-firmware | This fault typically occurs when the CIMC or BIOS firmware on a server is an earlier release than Cisco UCS, Release 1.4. | If you see this fault, consider upgrading the CIMC firmware, and the entire Cisco UCS instance if necessary, to Cisco UCS, Release 1.4 or later. | none | TRUE | environmental | power:Budget | sys/chassis-[id]/blade-[slotId]/budget | 798 | fltPowerBudgetFirmwareMismatch
F0801 | fltProcessorUnitIdentity-unestablishable | Processor [id] on server [chassisId]/[slotId] has an invalid FRUProcessor [id] on server [id] has an invalid FRU | warning | identity-unestablishable | This fault typically occurs because Cisco UCS Manager has detected an unsupported CPU in the server. For example, the model, vendor, or revision is not recognized. | If you see this fault, take the following actions: - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, you may have an unsupported CPU configuration in the server. Create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | processor:Unit | sys/chassis-[id]/blade-[slotId]/board/cpu-[id] | 801 | fltProcessorUnitIdentityUnestablishable
F0821 | fltIqnpoolPoolEmpty | iqn pool [name] is empty | minor | empty-pool | This fault typically occurs when an IQN pool does not contain any IQNs. | If you see this fault, take the following actions: - If the pool is in use, add a block of IQNs to the pool. - If the pool is not in use, ignore the fault. | none | TRUE | server | iqnpool:Pool | org-[name]/iqn-pool-[name] | 821 | fltIqnpoolPoolEmpty
F0831 | fltFabricDceSwSrvPcEpDown | [type] Member [slotId]/[portId] of Port-Channel [portId] on fabric interconnect [id] is down, membership: [membership] | major | membership-down | This fault typically occurs when a member port in a fabric port channel is down. | If you see this fault, take the following action: - Check the link connectivity between the FEX or IOM and the fabric interconnect. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:DceSwSrvPcEp | fabric/server/sw-[id]/pc-[portId]/ep-slot-[slotId]-port-[portId] | 831 | fltFabricDceSwSrvPcEpDown
F0832 | fltFabricEpMgrEpTransModeFail | Port constraint violation on switch [id]: [confQual] | critical | config-error | This fault occurs when at least one logical interface is misconfigured. This can happen when upgrading to a different type or series of fabric interconnect or when importing a configuration. The configuration must meet the following constraints: - The first Fibre Channel port must be an odd port number. This constraint cannot be violated when upgrading from a Cisco UCS 6100 series fabric interconnect to a Cisco UCS 6200 series fabric interconnect. - All FC ports must be configured contiguously with intervening unconfigured FC ports. This can happen during an upgrade from a Cisco UCS 6100 series fabric interconnect when you import the configuration from a Cisco UCS 6100 series fabric interconnect configuration into a Cisco UCS 6200 series fabric interconnect. For example, the Cisco UCS 6100 series fabric interconnect has an FC expansion module with ports FC2/1 through FC2/6 configured. When you import that configuration into a Cisco UCS 6200 series fabric interconnect, FC ports 2/7 through 2/16 remain unconfigured. You can correct this problem by configuring the missing FC ports. - Ethernet and FC port ranges cannot overlap. This can happen when upgrading from a Cisco UCS 6100 series fabric interconnect to a Cisco UCS 6200 series fabric interconnect. For example, some Cisco UCS 6100 expansion modules have FC and Ethernet ports with the same ID, such as FC port 2/1 and Ethernet port 2/1. - There must be at most one logical port per fabric interconnect ID/module ID/port ID. For example, a port cannot be configured as both Ethernet and FC. This can happen during an upgrade from a Cisco UCS 6100 series fabric interconnect. For example, some Cisco UCS 6100 expansion modules have FC and Ethernet ports with the same ID, such as FC port 2/1 and Ethernet port 2/1. - Within a module, the port IDs of Ethernet ports must be lower than the smallest FC port ID. This means that all Ethernet ports must be on the left and all FC ports on the right. This can happen during an upgrade from a Cisco UCS 6140 fabric interconnect with 40 ports on the fixed module to a Cisco UCS 6248 fabric interconnect with 32 ports on the fixed module. For example, if the Cisco UCS 6248 is initially configured with Ethernet ports 1/1 through 1/16 and FC ports 1/17 through 1/32, and you import a a configuration from the Cisco UCS 6140 with Ethernet ports 1/1 through 1/32 unconfigured and Ethernet ports 1/33 through 1/40, the resulting configuration is Ethernet 1/1 through 1/16, FC 1/17 through 1/32, and Ethernet 1/33 through 1/40. This is not a valid configuration. You must delete ports 1/33 through 1/40 to correct the configuration. - A non-unified Ethernet port cannot be configured as an FC port. Please note the following: - This constraint cannot be violated when upgrading from a Cisco UCS 6100 series fabric interconnect to a Cisco UCS 6200 series fabric interconnect. - This constraint can be violated when downgrading from a Cisco UCS 6200 series fabric interconnect to a Cisco UCS 6100 series fabric interconnect. - This constraint can be violated when pre-provisioning a port on a Cisco UCS 6100 series fabric interconnect and then inserting an expansion module that does not match the requirement. - A non-unified FC port cannot be configured as an Ethernet port. Please note the following: - This constraint cannot be violated when upgrading from a Cisco UCS 6100 series fabric interconnect to a Cisco UCS 6200 series fabric interconnect. - This constraint can be violated when downgrading from a Cisco UCS 6200 series fabric interconnect to a Cisco UCS 6100 series fabric interconnect. - This constraint can be violated when pre-provisioning a port on a Cisco UCS 6100 series fabric interconnect and then inserting an expansion module that does not match the requirement. - On a Cisco UCS 6100 series fabric interconnect, server ports cannot be configured on expansion modules. This constraint can be violated when downgrading from a Cisco UCS 6200 series fabric interconnect to a Cisco UCS 6100 series fabric interconnect. | If you see this fault, take the following action: - Create a list of all logical interfaces that are misconfigured and have caused an 'error-misconfigured' fault. - For each logical interface, note the reason listed in the fault for the misconfiguration. - Log into Cisco UCS Manager and correct each misconfigured logical interface. If you used the Cisco UCS Manager CLI, commit all changes. - Review any faults or error messages that describe additional misconfigurations and correct those errors. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:EpMgr | fabric/[id] | 832 | fltFabricEpMgrEpTransModeFail
F0833 | fltFabricVlanMisconfigured | VLAN [name] is [operState] because of conflicting vlan-id with an fcoe-vlan | critical | vlan-misconfigured | This fault typically occurs when VLAN has the same ID as an FCoE VLAN. This issue can cause disruption of traffic. | If you see this fault, take the following action: - Check the VLAN ID. - If the ID of the VLAN matches the ID of the FCoE VLAN assigned to a VLAN in the same fabric interconnect, change the ID of either the VLAN or the FCoE VLAN. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:Vlan | fabric/eth-estc/[id]/net-[name] | 833 | fltFabricVlanMisconfigured
F0834 | fltFabricPIoEpErrorMisconfigured | Interface [name] is [operState]. Reason: [operStateReason] | critical | interface-misconfigured | This fault occurs when a logical interface is misconfigured. This can happen when upgrading to a different type or series of fabric interconnect or when importing a configuration. | If you see this fault, take the following action: - Create a list of all logical interfaces that are misconfigured and have caused an 'error-misconfigured' fault. - For each logical interface, note the reason listed in the fault for the misconfiguration. - Log into Cisco UCS Manager and correct each misconfigured logical interface. If you used the Cisco UCS Manager CLI, commit all changes. - Review any faults or error messages that describe additional misconfigurations and correct those errors. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:PIoEp |  | 834 | fltFabricPIoEpErrorMisconfigured
F0835 | fltFabricEthLanEpMissingPrimaryVlan | Primary vlan missing from fabric: [switchId], port: [slotId]/[portId]. | major | missing-primary-vlan | This fault occurs when an uplink port or port channel is configured with a primary VLAN that does not exist in the Cisco UCS instance. | If you see this fault, take the following action: - Update the configuration of the port or port channel to include a primary VLAN. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | fabric:EthLanEp | fabric/lan/[id]/phys-slot-[slotId]-port-[portId] | 835 | fltFabricEthLanEpMissingPrimaryVlan
F0836 | fltFabricEthLanPcMissingPrimaryVlan | Primary vlan missing from fabric: [switchId], port-channel: [portId]. | major | missing-primary-vlan | This fault occurs when an uplink port or port channel is configured with a primary VLAN that does not exist in the Cisco UCS instance. | If you see this fault, take the following action: - Update the configuration of the port or port channel to include a primary VLAN. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | fabric:EthLanPc | fabric/lan/[id]/pc-[portId] | 836 | fltFabricEthLanPcMissingPrimaryVlan
F0840 | fltVnicEtherPinningMismatch | Hard pinning target for eth vNIC [name], service profile [name] does not have all the required vlans configured | warning | pinning-mismatch | This fault occurs when one or more VLANs required by vNIC in a service profile are not configured on the target uplink port or port channel for a hard-pinned LAN pin group. | If you see this fault, take the following actions: - In the LAN Uplinks Manager of the Cisco UCS Manager GUI, configure all of the VLANs in the vNIC in the target uplink port or port channel for the LAN pin group. If you prefer to use the Cisco UCS Manager CLI, navigate to scope /eth-uplink/vlan and create the required member ports for the LAN pin group. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | configuration | vnic:Ether | org-[name]/tier-[name]/ls-[name]/ether-[name] | 840 | fltVnicEtherPinningMismatch
F0841 | fltVnicEtherPinningMisconfig | Hard pinning target for eth vNIC [name], service profile [name] is missing or misconfigured | major | pinning-misconfig | This fault occurs when one or more vNIC target uplink ports or port channels for a hard-pinned LAN pin group are either missing or misconfigured as the wrong port type.</br | If you see this fault, take the following actions: - Review the LAN pin group configuration. - Correct the configuration of the port and port channels in the pin group. - Ensure that all required vLANs are allowed on the target ports or port channels. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | configuration | vnic:Ether | org-[name]/tier-[name]/ls-[name]/ether-[name] | 841 | fltVnicEtherPinningMisconfig
F0842 | fltProcessorUnitDisabled | Processor [id] on server [chassisId]/[slotId] operState: [operState]Processor [id] on server [id] operState: [operState] | info | equipment-disabled | This fault occurs in the unlikely event that a processor is disabled. | If you see this fault, take the following actions: - If this fault occurs on a blade server, remove and reinsert the server into the chassis. - In Cisco UCS Manager, decommission and recommission the blade server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | environmental | processor:Unit | sys/chassis-[id]/blade-[slotId]/board/cpu-[id] | 842 | fltProcessorUnitDisabled
F0843 | fltStorageLocalLunInoperable | Local LUN [id] on server [chassisId]/[slotId] operability: [operability]Local LUN [id] on server [id] operability: [operability] | major | equipment-inoperable | This fault occurs when a LUN has become inoperable | If you see this fault, take the following actions: - Make sure the remote storage LUN is accessible to the server. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | storage:LocalLun | sys/chassis-[id]/blade-[slotId]/board/storage-[type]-[id]/lun-[id] | 843 | fltStorageLocalLunInoperable
F0844 | fltMemoryUnitDisabled | DIMM [location] on server [chassisId]/[slotId] operState: [operState]DIMM [location] on server [id] operaState: [operState] | major | equipment-disabled | This fault is raised when the server BIOS disables a DIMM. The BIOS could disable a DIMM for several reasons, including incorrect location of the DIMM or incompatible speed. | If you see this fault, refer to the Cisco UCS B-Series Troubleshooting Guide for information on how to resolve the DIMM issues. | diagnostic | TRUE | equipment | memory:Unit | sys/chassis-[id]/blade-[slotId]/board/memarray-[id]/mem-[id] | 844 | fltMemoryUnitDisabled
F0856 | fltFirmwareBootUnitActivateStatusFailed | Activation failed and Activate Status set to failed. | warning | activation-failed | This fault typically occurs for the following reasons: when firmware activation fails, or if the after activation running image is not the corresponding startup image. - Firmware activation failed. - The version of firmware running on the server after activation is not the version listed in Cisco UCS Manager as the startup image. | If you see this fault, take the following actions: - Go to FSM tab for the endpoint on which the fault is raised and review the error description for the reason that the activation failed. - If the FSM failed, review the error message in the FSM. - If possible, correct the problem described in the error message. - If the problem persists, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | firmware:BootUnit | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/fw-boot-def/bootunit-[type] | 856 | fltFirmwareBootUnitActivateStatusFailed
F0858 | fltFabricInternalPcDown | [type] port-channel [portId] on fabric interconnect [id] oper state: [operState], reason: [stateQual] | major | operational-state-down | This fault occurs when the transport VIF for a server is down. Cisco UCS Manager raises this fault when a fabric interconnect reports the connectivity state on virtual interface as one of the following: - Down - Errored - Unavailable | If you see this fault, take the following actions: - Verify that the blade server discovery was successful. - Check the states on all communicating ports from end to end. - If connectivity seems correct, decommission and recommission the server. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | network | fabric:InternalPc |  | 858 | fltFabricInternalPcDown
F0863 | fltMgmtEntityDevice-1-shared-storage-error | device [chassis1], error accessing shared-storage | warning | device-shared-storage-error | This fault occurs in an unlikely event that the shared storage selected for writing the cluster state is not accessible. This impacts the full HA functionality of the fabric interconnect cluster. | If you see this fault, create a show tech-support file and contact Cisco TAC.lt;br/ | none | TRUE | management | mgmt:Entity | sys/mgmt-entity-[id] | 863 | fltMgmtEntityDevice1SharedStorageError
F0864 | fltMgmtEntityDevice-2-shared-storage error | device [chassis2], error accessing shared-storage | warning | device-shared-storage-error | This fault occurs in an unlikely event that the shared storage selected for writing the cluster state is not accessible. This impacts the full HA functionality of the fabric interconnect cluster. | If you see this fault, create a show tech-support file and contact Cisco TAC.lt;br/ | none | TRUE | management | mgmt:Entity | sys/mgmt-entity-[id] | 864 | fltMgmtEntityDevice2SharedStorageError
F0865 | fltMgmtEntityDevice-3-shared-storage error | device [chassis3], error accessing shared-storage | warning | device-shared-storage-error | This fault occurs in an unlikely event that the shared storage selected for writing the cluster state is not accessible. This impacts the full HA functionality of the fabric interconnect cluster. | If you see this fault, create a show tech-support file and contact Cisco TAC.lt;br/ | none | TRUE | management | mgmt:Entity | sys/mgmt-entity-[id] | 865 | fltMgmtEntityDevice3SharedStorageError
F0866 | fltMgmtEntityHa-ssh-keys-mismatched | Fabric Interconnect [id], management services, mismatched SSH keys | major | ha-ssh-keys-mismatched | This fault indicates that one of the following scenarios has occurred: - The internal SSH keys used for HA in the cluster configuration are mismatched. This causes certain operations to fail. - Another fabric interconnect is connected to the primary fabric interconnect in the cluster without first erasing the existing configuration in the primary. | If you see this fault, take the following actions: - Log into the Cisco UCS Manager CLI on the subordinate fabric interconnect. - Enter connect local-mgmt - Enter erase configuration to erase the configuration on the subordinate fabric interconnect and reboot it. - When the secondary fabric interconnect has rebooted, reconfigure it for the cluster. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | mgmt:Entity | sys/mgmt-entity-[id] | 866 | fltMgmtEntityHaSshKeysMismatched
F0867 | fltMgmtPmonEntryUCSM process failure | UCSM process [name] failed on FI [switchId] | critical | ucsm-process-failure | This fault occurs in an unlikely event of a Cisco UCS Manager process crash. Typically, the failed process restarts and recovers from the problem. Any pending operations are restarted after the process successfully restarts. | If you see this fault and the process does not restart successfully, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | mgmt:PmonEntry | sys/mgmt-entity-[id]/[name] | 867 | fltMgmtPmonEntryUCSMProcessFailure
F0868 | fltComputeBoardPowerFail | Motherboard of server [chassisId]/[slotId] (service profile: [assignedToDn]) power: [power]Motherboard of server [id] (service profile: [assignedToDn]) power: [power] | critical | power-problem | This fault typically occurs when the power sensors on a blade server detect a problem. | If you see this fault, take the following actions: - Remove the blade server from the chassis. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | environmental | compute:Board | sys/chassis-[id]/blade-[slotId]/board | 868 | fltComputeBoardPowerFail
F0869 | fltComputeBoardThermalProblem | Motherboard of server [chassisId]/[slotId] (service profile: [assignedToDn]) thermal: [thermal]Motherboard of server [id] (service profile: [assignedToDn]) thermal: [thermal] | minor | thermal-problem | This fault typically occurs when the motherboard thermal sensors on a server detect a problem. | If you see this fault, take the following actions: - Verify that the server fans are working properly. - Wait for 24 hours to see if the problem resolves itself. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | compute:Board | sys/chassis-[id]/blade-[slotId]/board | 869 | fltComputeBoardThermalProblem
F0876 | fltVmVifLinkState | Virtual interface [vifId] link is down; reason [stateQual] | minor | vif-down | This fault occurs when Cisco UCS cannot send or receive data through an uplink port. | If you see this fault, take the following actions: - Enable the failed uplink port. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | management | vm:Vif | vmm/computeEp-[uuid]/nic-[name]/sw-[phSwitchId]vif-[vifId] | 876 | fltVmVifLinkState
F0881 | fltEquipmentPsuPowerSupplyShutdown | Power supply [id] in chassis [id] shutdown reason:[powerStateQualifier] | major | equipment-offline | This fault typically occurs when a power supply unit in a chassis, fabric interconnect, or a FEX is shut down, either due to higher than expected power current, higher than expected temperatures, or the failure of a fan. | If you see this fault, take the following actions: - Review the product specifications to determine the temperature operating range of the server. - Review the Cisco UCS Site Preparation Guide to ensure the servers have adequate airflow, including front and back clearance. - Verify that the air flows on the Cisco UCS chassis or rack server are not obstructed. - Verify that the site cooling system is operating properly. - Power off unused blade servers and rack servers. - Verify that the power cord is properly connected to the PSU and the power source. - Verify that the power source is 220 volts. - Verify that the PSU is properly installed in the chassis or fabric interconnect. - Remove the PSU and reinstall it. - Replace the PSU. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | environmental | TRUE | environmental | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 881 | fltEquipmentPsuPowerSupplyShutdown
F0882 | fltEquipmentPsuPowerThreshold | Power supply [id] on chassis [id] has exceeded its power thresholdPower supply [id] on server [id] has exceeded its power threshold | critical | power-problem | This fault occurs when a power supply unit is drawing too much current. | If you see this fault, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 882 | fltEquipmentPsuPowerThreshold
F0883 | fltEquipmentPsuInputError | Power supply [id] on chassis [id] has disconnected cable or bad input voltagePower supply [id] on server [id] has disconnected cable or bad input voltage | critical | power-problem | This fault occurs when a power cable is disconnected or input voltage is incorrect. | If you see this fault, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:Psu | sys/rack-unit-[id]/psu-[id] | 883 | fltEquipmentPsuInputError
F0884 | fltEquipmentSwitchCardPowerOff | Switch card is powered down. | critical | power-down | This fault occurs when the switch card is powered down. | If you see this fault, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:SwitchCard | sys/switch-[id]/slot-[id] | 884 | fltEquipmentSwitchCardPowerOff
F0885 | fltNetworkElementInventoryFailed | Fabric Interconnect [id] inventory is not complete: [inventoryStatus] | major | inventory-failed | Cisco UCS Manager raises this fault when the management subsystem is unable to perform an inventory of the physical components, such as I/O cards or physical ports. | If you see this fault, take the following actions: - Ensure that both fabric interconnects in an HA cluster are running the same software versions. - Ensure that the fabric interconnect software is a version that is compatible with the Cisco UCS Manager software. - If the above actions did not resolve the issue, create a show tech-support file and contact Cisco TAC. | diagnostic | TRUE | equipment | network:Element | sys/switch-[id] | 885 | fltNetworkElementInventoryFailed
F0900 | fltAdaptorUnitExtnUnidentifiable-fru | Adapter extension [id] in server [chassisId]/[slotId] has unidentified FRU | major | unidentifiable-fru | This fault typically occurs because Cisco UCS Manager has detected an unsupported adapter unit extension, such as a pass-through adaptor. For example, the model, vendor, or revision is not recognized. | If you see this fault, take the following actions: - Verify that a supported adapter unit extension is installed. - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | server | adaptor:UnitExtn | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/adaptor-extn-[id] | 900 | fltAdaptorUnitExtnUnidentifiableFru
F0901 | fltAdaptorUnitExtnMissing | Adapter extension [id] in server [chassisId]/[slotId] presence: [presence] | warning | equipment-missing | This fault typically occurs when an I/O adapter unit extension, such as a pass-through adapter, is missing. Cisco UCS Manager raises this fault when any of the following scenario occur: - The endpoint reports there is no adapter unit extension, such as a pass-through adapter, plugged into the adapter slot. - The endpoint cannot detect or communicate with the adapter unit extension plugged into the adapter slot. | If you see this fault, take the following actions: - Ensure the adapter unit extension is properly plugged into an adapter slot in the server. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | adaptor:UnitExtn | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/adaptor-extn-[id] | 901 | fltAdaptorUnitExtnMissing
F0902 | fltEquipmentFexFex-unsupported | Fex [id] with model [model] is unsupported | major | fex-unsupported | This fault typically occurs because Cisco UCS Manager has detected an unsupported FEX. For example, the model, vendor, or revision is not recognized. | If you see this fault, take the following actions: - Verify that a supported FEX is installed. - Verify that the capability catalog in Cisco UCS Manager is up to date. If necessary, update the catalog. - If the above action did not resolve the issue, create a show tech-support file and contact Cisco TAC. | none | TRUE | equipment | equipment:Fex | sys/fex-[id] | 902 | fltEquipmentFexFexUnsupported
F16405 | fsmStFailEquipmentIOCardFePresence:CheckLicense | [FSM:STAGE:FAILED¦RETRY]: Checking license for chassis [chassisId] (iom [id])(FSM-STAGE:sam:dme:EquipmentIOCardFePresence:CheckLicense) | warning | check-license-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 16405 | fsmStFailEquipmentIOCardFePresenceCheckLicense
F16405 | fsmStFailEquipmentIOCardFePresence:Identify | [FSM:STAGE:FAILED¦RETRY]: identifying IOM [chassisId]/[id](FSM-STAGE:sam:dme:EquipmentIOCardFePresence:Identify) | warning | identify-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 16405 | fsmStFailEquipmentIOCardFePresenceIdentify
F16406 | fsmStFailEquipmentIOCardFeConn:ConfigureEndPoint | [FSM:STAGE:FAILED¦RETRY]: configuring management identity to IOM [chassisId]/[id]([side])(FSM-STAGE:sam:dme:EquipmentIOCardFeConn:ConfigureEndPoint) | warning | configure-end-point-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 16406 | fsmStFailEquipmentIOCardFeConnConfigureEndPoint
F16406 | fsmStFailEquipmentIOCardFeConn:ConfigureSwMgmtEndPoint | [FSM:STAGE:FAILED¦RETRY]: configuring fabric interconnect [switchId] mgmt connectivity to IOM [chassisId]/[id]([side])(FSM-STAGE:sam:dme:EquipmentIOCardFeConn:ConfigureSwMgmtEndPoint) | warning | configure-sw-mgmt-end-point-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 16406 | fsmStFailEquipmentIOCardFeConnConfigureSwMgmtEndPoint
F16406 | fsmStFailEquipmentIOCardFeConn:ConfigureVifNs | [FSM:STAGE:FAILED¦RETRY]: configuring IOM [chassisId]/[id]([side]) virtual name space(FSM-STAGE:sam:dme:EquipmentIOCardFeConn:ConfigureVifNs) | warning | configure-vif-ns-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 16406 | fsmStFailEquipmentIOCardFeConnConfigureVifNs
F16406 | fsmStFailEquipmentIOCardFeConn:DiscoverChassis | [FSM:STAGE:FAILED¦RETRY]: triggerring chassis discovery via IOM [chassisId]/[id]([side])(FSM-STAGE:sam:dme:EquipmentIOCardFeConn:DiscoverChassis) | warning | discover-chassis-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 16406 | fsmStFailEquipmentIOCardFeConnDiscoverChassis
F16406 | fsmStFailEquipmentIOCardFeConn:EnableChassis | [FSM:STAGE:FAILED¦RETRY]: enabling chassis [chassisId] on [side] side(FSM-STAGE:sam:dme:EquipmentIOCardFeConn:EnableChassis) | warning | enable-chassis-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 16406 | fsmStFailEquipmentIOCardFeConnEnableChassis
F16407 | fsmStFailEquipmentChassisRemoveChassis:DisableEndPoint | [FSM:STAGE:FAILED¦RETRY]: unconfiguring access to chassis [id](FSM-STAGE:sam:dme:EquipmentChassisRemoveChassis:DisableEndPoint) | warning | disable-end-point-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 16407 | fsmStFailEquipmentChassisRemoveChassisDisableEndPoint
F16407 | fsmStFailEquipmentChassisRemoveChassis:UnIdentifyLocal | [FSM:STAGE:FAILED¦RETRY]: erasing chassis identity [id] from primary(FSM-STAGE:sam:dme:EquipmentChassisRemoveChassis:UnIdentifyLocal) | warning | un-identify-local-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 16407 | fsmStFailEquipmentChassisRemoveChassisUnIdentifyLocal
F16407 | fsmStFailEquipmentChassisRemoveChassis:UnIdentifyPeer | [FSM:STAGE:FAILED¦RETRY]: erasing chassis identity [id] from secondary(FSM-STAGE:sam:dme:EquipmentChassisRemoveChassis:UnIdentifyPeer) | warning | un-identify-peer-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 16407 | fsmStFailEquipmentChassisRemoveChassisUnIdentifyPeer
F16407 | fsmStFailEquipmentChassisRemoveChassis:Wait | [FSM:STAGE:FAILED¦RETRY]: waiting for clean up of resources for chassis [id] (approx. 2 min)(FSM-STAGE:sam:dme:EquipmentChassisRemoveChassis:Wait) | warning | wait-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 16407 | fsmStFailEquipmentChassisRemoveChassisWait
F16407 | fsmStFailEquipmentChassisRemoveChassis:decomission | [FSM:STAGE:FAILED¦RETRY]: decomissioning chassis [id](FSM-STAGE:sam:dme:EquipmentChassisRemoveChassis:decomission) | warning | decomission-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 16407 | fsmStFailEquipmentChassisRemoveChassisDecomission
F16408 | fsmStFailEquipmentLocatorLedSetLocatorLed:Execute | [FSM:STAGE:FAILED¦RETRY]: setting locator led to [adminState](FSM-STAGE:sam:dme:EquipmentLocatorLedSetLocatorLed:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:LocatorLed | sys/chassis-[id]/blade-[slotId]/locator-led | 16408 | fsmStFailEquipmentLocatorLedSetLocatorLedExecute
F16518 | fsmStFailMgmtControllerExtMgmtIfConfig:Primary | [FSM:STAGE:FAILED¦RETRY]: external mgmt interface configuration on primary(FSM-STAGE:sam:dme:MgmtControllerExtMgmtIfConfig:Primary) | warning | primary-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16518 | fsmStFailMgmtControllerExtMgmtIfConfigPrimary
F16518 | fsmStFailMgmtControllerExtMgmtIfConfig:Secondary | [FSM:STAGE:FAILED¦RETRY]: external mgmt interface configuration on secondary(FSM-STAGE:sam:dme:MgmtControllerExtMgmtIfConfig:Secondary) | warning | secondary-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16518 | fsmStFailMgmtControllerExtMgmtIfConfigSecondary
F16519 | fsmStFailFabricComputeSlotEpIdentify:ExecuteLocal | [FSM:STAGE:FAILED¦RETRY]: identifying a server in [chassisId]/[slotId] via CIMC(FSM-STAGE:sam:dme:FabricComputeSlotEpIdentify:ExecuteLocal) | warning | execute-local-failed | None set. | None set. | none | TRUE | fsm | fabric:ComputeSlotEp | fabric/server/chassis-[chassisId]/slot-[slotId] | 16519 | fsmStFailFabricComputeSlotEpIdentifyExecuteLocal
F16519 | fsmStFailFabricComputeSlotEpIdentify:ExecutePeer | [FSM:STAGE:FAILED¦RETRY]: identifying a server in [chassisId]/[slotId] via CIMC(FSM-STAGE:sam:dme:FabricComputeSlotEpIdentify:ExecutePeer) | warning | execute-peer-failed | None set. | None set. | none | TRUE | fsm | fabric:ComputeSlotEp | fabric/server/chassis-[chassisId]/slot-[slotId] | 16519 | fsmStFailFabricComputeSlotEpIdentifyExecutePeer
F16520 | fsmStFailComputeBladeDiscover:BiosPostCompletion | [FSM:STAGE:FAILED¦RETRY]: Waiting for BIOS POST completion from CIMC on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:BiosPostCompletion) | warning | bios-post-completion-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBiosPostCompletion
F16520 | fsmStFailComputeBladeDiscover:BladeBootPnuos | [FSM:STAGE:FAILED¦RETRY]: power server [chassisId]/[slotId] on with pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:BladeBootPnuos) | warning | blade-boot-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBladeBootPnuos
F16520 | fsmStFailComputeBladeDiscover:BladeBootWait | [FSM:STAGE:FAILED¦RETRY]: Waiting for system reset on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:BladeBootWait) | warning | blade-boot-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBladeBootWait
F16520 | fsmStFailComputeBladeDiscover:BladePowerOn | [FSM:STAGE:FAILED¦RETRY]: power on server [chassisId]/[slotId] for discovery(FSM-STAGE:sam:dme:ComputeBladeDiscover:BladePowerOn) | warning | blade-power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBladePowerOn
F16520 | fsmStFailComputeBladeDiscover:BladeReadSmbios | [FSM:STAGE:FAILED¦RETRY]: Waiting for SMBIOS table from CIMC on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:BladeReadSmbios) | warning | blade-read-smbios-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBladeReadSmbios
F16520 | fsmStFailComputeBladeDiscover:BmcConfigPnuOS | [FSM:STAGE:FAILED¦RETRY]: provisioning a bootable device with a bootable pre-boot image for server(FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcConfigPnuOS) | warning | bmc-config-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBmcConfigPnuOS
F16520 | fsmStFailComputeBladeDiscover:BmcInventory | [FSM:STAGE:FAILED¦RETRY]: getting inventory of server [chassisId]/[slotId] via CIMC(FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcInventory) | warning | bmc-inventory-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBmcInventory
F16520 | fsmStFailComputeBladeDiscover:BmcPreConfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcPreConfigPnuOSLocal) | warning | bmc-pre-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBmcPreConfigPnuOSLocal
F16520 | fsmStFailComputeBladeDiscover:BmcPreConfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcPreConfigPnuOSPeer) | warning | bmc-pre-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBmcPreConfigPnuOSPeer
F16520 | fsmStFailComputeBladeDiscover:BmcPresence | [FSM:STAGE:FAILED¦RETRY]: checking CIMC of server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcPresence) | warning | bmc-presence-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBmcPresence
F16520 | fsmStFailComputeBladeDiscover:BmcShutdownDiscovered | [FSM:STAGE:FAILED¦RETRY]: Shutdown the server [chassisId]/[slotId]; deep discovery completed(FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcShutdownDiscovered) | warning | bmc-shutdown-discovered-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverBmcShutdownDiscovered
F16520 | fsmStFailComputeBladeDiscover:ConfigFeLocal | [FSM:STAGE:FAILED¦RETRY]: configuring primary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:ConfigFeLocal) | warning | config-fe-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverConfigFeLocal
F16520 | fsmStFailComputeBladeDiscover:ConfigFePeer | [FSM:STAGE:FAILED¦RETRY]: configuring secondary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:ConfigFePeer) | warning | config-fe-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverConfigFePeer
F16520 | fsmStFailComputeBladeDiscover:ConfigUserAccess | [FSM:STAGE:FAILED¦RETRY]: configuring external user access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:ConfigUserAccess) | warning | config-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverConfigUserAccess
F16520 | fsmStFailComputeBladeDiscover:HandlePooling | [FSM:STAGE:FAILED¦RETRY]: Invoke post-discovery policies on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:HandlePooling) | warning | handle-pooling-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverHandlePooling
F16520 | fsmStFailComputeBladeDiscover:NicConfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: configure primary adapter in [chassisId]/[slotId] for pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:NicConfigPnuOSLocal) | warning | nic-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverNicConfigPnuOSLocal
F16520 | fsmStFailComputeBladeDiscover:NicConfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: configure secondary adapter in [chassisId]/[slotId] for pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:NicConfigPnuOSPeer) | warning | nic-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverNicConfigPnuOSPeer
F16520 | fsmStFailComputeBladeDiscover:NicPresenceLocal | [FSM:STAGE:FAILED¦RETRY]: detect mezz cards in [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:NicPresenceLocal) | warning | nic-presence-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverNicPresenceLocal
F16520 | fsmStFailComputeBladeDiscover:NicPresencePeer | [FSM:STAGE:FAILED¦RETRY]: detect mezz cards in [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:NicPresencePeer) | warning | nic-presence-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverNicPresencePeer
F16520 | fsmStFailComputeBladeDiscover:NicUnconfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfigure adapter of server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:NicUnconfigPnuOSLocal) | warning | nic-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverNicUnconfigPnuOSLocal
F16520 | fsmStFailComputeBladeDiscover:NicUnconfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfigure adapter of server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:NicUnconfigPnuOSPeer) | warning | nic-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverNicUnconfigPnuOSPeer
F16520 | fsmStFailComputeBladeDiscover:PnuOSCatalog | [FSM:STAGE:FAILED¦RETRY]: Populate pre-boot catalog to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSCatalog) | warning | pnuoscatalog-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverPnuOSCatalog
F16520 | fsmStFailComputeBladeDiscover:PnuOSIdent | [FSM:STAGE:FAILED¦RETRY]: Identify pre-boot environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSIdent) | warning | pnuosident-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverPnuOSIdent
F16520 | fsmStFailComputeBladeDiscover:PnuOSInventory | [FSM:STAGE:FAILED¦RETRY]: Perform inventory of server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSInventory) | warning | pnuosinventory-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverPnuOSInventory
F16520 | fsmStFailComputeBladeDiscover:PnuOSPolicy | [FSM:STAGE:FAILED¦RETRY]: Populate pre-boot environment behavior policy to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSPolicy) | warning | pnuospolicy-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverPnuOSPolicy
F16520 | fsmStFailComputeBladeDiscover:PnuOSScrub | [FSM:STAGE:FAILED¦RETRY]: Scrub server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSScrub) | warning | pnuosscrub-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverPnuOSScrub
F16520 | fsmStFailComputeBladeDiscover:PnuOSSelfTest | [FSM:STAGE:FAILED¦RETRY]: Trigger self-test of server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSSelfTest) | warning | pnuosself-test-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverPnuOSSelfTest
F16520 | fsmStFailComputeBladeDiscover:PreSanitize | [FSM:STAGE:FAILED¦RETRY]: Preparing to check hardware configuration server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverPreSanitize
F16520 | fsmStFailComputeBladeDiscover:Sanitize | [FSM:STAGE:FAILED¦RETRY]: Checking hardware configuration server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSanitize
F16520 | fsmStFailComputeBladeDiscover:SetupVmediaLocal | [FSM:STAGE:FAILED¦RETRY]: provisioning a Virtual Media device with a bootable pre-boot image for blade [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:SetupVmediaLocal) | warning | setup-vmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSetupVmediaLocal
F16520 | fsmStFailComputeBladeDiscover:SetupVmediaPeer | [FSM:STAGE:FAILED¦RETRY]: provisioning a Virtual Media device with a bootable pre-boot image for blade [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:SetupVmediaPeer) | warning | setup-vmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSetupVmediaPeer
F16520 | fsmStFailComputeBladeDiscover:SolRedirectDisable | [FSM:STAGE:FAILED¦RETRY]: Disable Sol Redirection on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:SolRedirectDisable) | warning | sol-redirect-disable-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSolRedirectDisable
F16520 | fsmStFailComputeBladeDiscover:SolRedirectEnable | [FSM:STAGE:FAILED¦RETRY]: set up bios token on server [chassisId]/[slotId] for Sol redirect(FSM-STAGE:sam:dme:ComputeBladeDiscover:SolRedirectEnable) | warning | sol-redirect-enable-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSolRedirectEnable
F16520 | fsmStFailComputeBladeDiscover:SwConfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: configure primary fabric interconnect in [chassisId]/[slotId] for pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:SwConfigPnuOSLocal) | warning | sw-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSwConfigPnuOSLocal
F16520 | fsmStFailComputeBladeDiscover:SwConfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: configure secondary fabric interconnect in [chassisId]/[slotId] for pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:SwConfigPnuOSPeer) | warning | sw-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSwConfigPnuOSPeer
F16520 | fsmStFailComputeBladeDiscover:SwUnconfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfigure primary fabric interconnect for server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:SwUnconfigPnuOSLocal) | warning | sw-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSwUnconfigPnuOSLocal
F16520 | fsmStFailComputeBladeDiscover:SwUnconfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfigure secondary fabric interconnect for server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:SwUnconfigPnuOSPeer) | warning | sw-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSwUnconfigPnuOSPeer
F16520 | fsmStFailComputeBladeDiscover:TeardownVmediaLocal | [FSM:STAGE:FAILED¦RETRY]: unprovisioning the Virtual Media bootable device for blade [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:TeardownVmediaLocal) | warning | teardown-vmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverTeardownVmediaLocal
F16520 | fsmStFailComputeBladeDiscover:TeardownVmediaPeer | [FSM:STAGE:FAILED¦RETRY]: unprovisioning the Virtual media bootable device for blade [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:TeardownVmediaPeer) | warning | teardown-vmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverTeardownVmediaPeer
F16520 | fsmStFailComputeBladeDiscover:hagConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to pre-boot environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:hagConnect) | warning | hag-connect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverHagConnect
F16520 | fsmStFailComputeBladeDiscover:hagDisconnect | [FSM:STAGE:FAILED¦RETRY]: Disconnect pre-boot environment agent for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:hagDisconnect) | warning | hag-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverHagDisconnect
F16520 | fsmStFailComputeBladeDiscover:serialDebugConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to pre-boot environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:serialDebugConnect) | warning | serial-debug-connect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSerialDebugConnect
F16520 | fsmStFailComputeBladeDiscover:serialDebugDisconnect | [FSM:STAGE:FAILED¦RETRY]: Disconnect pre-boot environment agent for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:serialDebugDisconnect) | warning | serial-debug-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16520 | fsmStFailComputeBladeDiscoverSerialDebugDisconnect
F16520 | fsmStFailComputeRackUnitDiscover:BiosPostCompletion | [FSM:STAGE:FAILED¦RETRY]: Waiting for BIOS POST completion from CIMC on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BiosPostCompletion) | warning | bios-post-completion-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBiosPostCompletion
F16520 | fsmStFailComputeRackUnitDiscover:BmcConfigPnuOS | [FSM:STAGE:FAILED¦RETRY]: provisioning a bootable device with a bootable pre-boot image for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcConfigPnuOS) | warning | bmc-config-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBmcConfigPnuOS
F16520 | fsmStFailComputeRackUnitDiscover:BmcConfigureConnLocal | [FSM:STAGE:FAILED¦RETRY]: Configuring connectivity on CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcConfigureConnLocal) | warning | bmc-configure-conn-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBmcConfigureConnLocal
F16520 | fsmStFailComputeRackUnitDiscover:BmcConfigureConnPeer | [FSM:STAGE:FAILED¦RETRY]: Configuring connectivity on CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcConfigureConnPeer) | warning | bmc-configure-conn-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBmcConfigureConnPeer
F16520 | fsmStFailComputeRackUnitDiscover:BmcInventory | [FSM:STAGE:FAILED¦RETRY]: getting inventory of server [id] via CIMC(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcInventory) | warning | bmc-inventory-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBmcInventory
F16520 | fsmStFailComputeRackUnitDiscover:BmcPreconfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcPreconfigPnuOSLocal) | warning | bmc-preconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBmcPreconfigPnuOSLocal
F16520 | fsmStFailComputeRackUnitDiscover:BmcPreconfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcPreconfigPnuOSPeer) | warning | bmc-preconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBmcPreconfigPnuOSPeer
F16520 | fsmStFailComputeRackUnitDiscover:BmcPresence | [FSM:STAGE:FAILED¦RETRY]: checking CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcPresence) | warning | bmc-presence-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBmcPresence
F16520 | fsmStFailComputeRackUnitDiscover:BmcShutdownDiscovered | [FSM:STAGE:FAILED¦RETRY]: Shutdown the server [id]; deep discovery completed(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcShutdownDiscovered) | warning | bmc-shutdown-discovered-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBmcShutdownDiscovered
F16520 | fsmStFailComputeRackUnitDiscover:BmcUnconfigPnuOS | [FSM:STAGE:FAILED¦RETRY]: unprovisioning the bootable device for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcUnconfigPnuOS) | warning | bmc-unconfig-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBmcUnconfigPnuOS
F16520 | fsmStFailComputeRackUnitDiscover:BootPnuos | [FSM:STAGE:FAILED¦RETRY]: power server [id] on with pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BootPnuos) | warning | boot-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBootPnuos
F16520 | fsmStFailComputeRackUnitDiscover:BootWait | [FSM:STAGE:FAILED¦RETRY]: Waiting for system reset on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BootWait) | warning | boot-wait-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverBootWait
F16520 | fsmStFailComputeRackUnitDiscover:ConfigDiscoveryMode | [FSM:STAGE:FAILED¦RETRY]: setting adapter mode to discovery for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:ConfigDiscoveryMode) | warning | config-discovery-mode-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverConfigDiscoveryMode
F16520 | fsmStFailComputeRackUnitDiscover:ConfigNivMode | [FSM:STAGE:FAILED¦RETRY]: setting adapter mode to NIV for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:ConfigNivMode) | warning | config-niv-mode-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverConfigNivMode
F16520 | fsmStFailComputeRackUnitDiscover:ConfigUserAccess | [FSM:STAGE:FAILED¦RETRY]: configuring external user access to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:ConfigUserAccess) | warning | config-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverConfigUserAccess
F16520 | fsmStFailComputeRackUnitDiscover:HandlePooling | [FSM:STAGE:FAILED¦RETRY]: Invoke post-discovery policies on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:HandlePooling) | warning | handle-pooling-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverHandlePooling
F16520 | fsmStFailComputeRackUnitDiscover:NicInventoryLocal | [FSM:STAGE:FAILED¦RETRY]: detect and get mezz cards information from [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:NicInventoryLocal) | warning | nic-inventory-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverNicInventoryLocal
F16520 | fsmStFailComputeRackUnitDiscover:NicInventoryPeer | [FSM:STAGE:FAILED¦RETRY]: detect and get mezz cards information from [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:NicInventoryPeer) | warning | nic-inventory-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverNicInventoryPeer
F16520 | fsmStFailComputeRackUnitDiscover:PnuOSCatalog | [FSM:STAGE:FAILED¦RETRY]: Populate pre-boot catalog to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSCatalog) | warning | pnuoscatalog-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverPnuOSCatalog
F16520 | fsmStFailComputeRackUnitDiscover:PnuOSConnStatus | [FSM:STAGE:FAILED¦RETRY]: Explore connectivity of server [id] in pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSConnStatus) | warning | pnuosconn-status-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverPnuOSConnStatus
F16520 | fsmStFailComputeRackUnitDiscover:PnuOSConnectivity | [FSM:STAGE:FAILED¦RETRY]: Explore connectivity of server [id] in pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSConnectivity) | warning | pnuosconnectivity-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverPnuOSConnectivity
F16520 | fsmStFailComputeRackUnitDiscover:PnuOSIdent | [FSM:STAGE:FAILED¦RETRY]: Identify pre-boot environment agent on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSIdent) | warning | pnuosident-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverPnuOSIdent
F16520 | fsmStFailComputeRackUnitDiscover:PnuOSInventory | [FSM:STAGE:FAILED¦RETRY]: Perform inventory of server [id] pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSInventory) | warning | pnuosinventory-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverPnuOSInventory
F16520 | fsmStFailComputeRackUnitDiscover:PnuOSPolicy | [FSM:STAGE:FAILED¦RETRY]: Populate pre-boot environment behavior policy to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSPolicy) | warning | pnuospolicy-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverPnuOSPolicy
F16520 | fsmStFailComputeRackUnitDiscover:PnuOSScrub | [FSM:STAGE:FAILED¦RETRY]: Scrub server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSScrub) | warning | pnuosscrub-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverPnuOSScrub
F16520 | fsmStFailComputeRackUnitDiscover:PnuOSSelfTest | [FSM:STAGE:FAILED¦RETRY]: Trigger self-test of server [id] pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSSelfTest) | warning | pnuosself-test-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverPnuOSSelfTest
F16520 | fsmStFailComputeRackUnitDiscover:PreSanitize | [FSM:STAGE:FAILED¦RETRY]: Preparing to check hardware configuration server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverPreSanitize
F16520 | fsmStFailComputeRackUnitDiscover:ReadSmbios | [FSM:STAGE:FAILED¦RETRY]: Waiting for SMBIOS table from CIMC on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:ReadSmbios) | warning | read-smbios-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverReadSmbios
F16520 | fsmStFailComputeRackUnitDiscover:Sanitize | [FSM:STAGE:FAILED¦RETRY]: Checking hardware configuration server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSanitize
F16520 | fsmStFailComputeRackUnitDiscover:SolRedirectDisable | [FSM:STAGE:FAILED¦RETRY]: Disable Sol Redirection on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SolRedirectDisable) | warning | sol-redirect-disable-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSolRedirectDisable
F16520 | fsmStFailComputeRackUnitDiscover:SolRedirectEnable | [FSM:STAGE:FAILED¦RETRY]: set up bios token on server [id] for Sol redirect(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SolRedirectEnable) | warning | sol-redirect-enable-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSolRedirectEnable
F16520 | fsmStFailComputeRackUnitDiscover:SwConfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: configure primary fabric interconnect for pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigPnuOSLocal) | warning | sw-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSwConfigPnuOSLocal
F16520 | fsmStFailComputeRackUnitDiscover:SwConfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: configure secondary fabric interconnect for pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigPnuOSPeer) | warning | sw-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSwConfigPnuOSPeer
F16520 | fsmStFailComputeRackUnitDiscover:SwConfigPortNivLocal | [FSM:STAGE:FAILED¦RETRY]: configuring primary fabric interconnect access to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigPortNivLocal) | warning | sw-config-port-niv-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSwConfigPortNivLocal
F16520 | fsmStFailComputeRackUnitDiscover:SwConfigPortNivPeer | [FSM:STAGE:FAILED¦RETRY]: configuring secondary fabric interconnect access to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigPortNivPeer) | warning | sw-config-port-niv-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSwConfigPortNivPeer
F16520 | fsmStFailComputeRackUnitDiscover:SwConfigureConnLocal | [FSM:STAGE:FAILED¦RETRY]: Configuring fabric-interconnect connectivity to CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigureConnLocal) | warning | sw-configure-conn-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSwConfigureConnLocal
F16520 | fsmStFailComputeRackUnitDiscover:SwConfigureConnPeer | [FSM:STAGE:FAILED¦RETRY]: Configuring fabric-interconnect connectivity to CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigureConnPeer) | warning | sw-configure-conn-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSwConfigureConnPeer
F16520 | fsmStFailComputeRackUnitDiscover:SwPnuOSConnectivityLocal | [FSM:STAGE:FAILED¦RETRY]: determine connectivity of server [id] to fabric(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwPnuOSConnectivityLocal) | warning | sw-pnuosconnectivity-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSwPnuOSConnectivityLocal
F16520 | fsmStFailComputeRackUnitDiscover:SwPnuOSConnectivityPeer | [FSM:STAGE:FAILED¦RETRY]: determine connectivity of server [id] to fabric(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwPnuOSConnectivityPeer) | warning | sw-pnuosconnectivity-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSwPnuOSConnectivityPeer
F16520 | fsmStFailComputeRackUnitDiscover:SwUnconfigPortNivLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfiguring primary fabric interconnect access to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwUnconfigPortNivLocal) | warning | sw-unconfig-port-niv-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSwUnconfigPortNivLocal
F16520 | fsmStFailComputeRackUnitDiscover:SwUnconfigPortNivPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfiguring secondary fabric interconnect access to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwUnconfigPortNivPeer) | warning | sw-unconfig-port-niv-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSwUnconfigPortNivPeer
F16520 | fsmStFailComputeRackUnitDiscover:hagConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to pre-boot environment agent on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:hagConnect) | warning | hag-connect-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverHagConnect
F16520 | fsmStFailComputeRackUnitDiscover:hagDisconnect | [FSM:STAGE:FAILED¦RETRY]: Disconnect pre-boot environment agent for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:hagDisconnect) | warning | hag-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverHagDisconnect
F16520 | fsmStFailComputeRackUnitDiscover:serialDebugConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to pre-boot environment agent on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:serialDebugConnect) | warning | serial-debug-connect-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSerialDebugConnect
F16520 | fsmStFailComputeRackUnitDiscover:serialDebugDisconnect | [FSM:STAGE:FAILED¦RETRY]: Disconnect pre-boot environment agent for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:serialDebugDisconnect) | warning | serial-debug-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverSerialDebugDisconnect
F16520 | fsmStFailComputeRackUnitDiscover:waitForConnReady | [FSM:STAGE:FAILED¦RETRY]: wait for connection to be established(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:waitForConnReady) | warning | wait-for-conn-ready-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 16520 | fsmStFailComputeRackUnitDiscoverWaitForConnReady
F16533 | fsmStFailEquipmentChassisPsuPolicyConfig:Execute | [FSM:STAGE:FAILED¦RETRY]: Deploying Power Management policy changes on chassis [id](FSM-STAGE:sam:dme:EquipmentChassisPsuPolicyConfig:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 16533 | fsmStFailEquipmentChassisPsuPolicyConfigExecute
F16534 | fsmStFailAdaptorHostFcIfResetFcPersBinding:ExecuteLocal | [FSM:STAGE:FAILED¦RETRY]: Resetting FC persistent bindings on host interface [dn](FSM-STAGE:sam:dme:AdaptorHostFcIfResetFcPersBinding:ExecuteLocal) | warning | execute-local-failed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 16534 | fsmStFailAdaptorHostFcIfResetFcPersBindingExecuteLocal
F16534 | fsmStFailAdaptorHostFcIfResetFcPersBinding:ExecutePeer | [FSM:STAGE:FAILED¦RETRY]: Resetting FC persistent bindings on host interface [dn](FSM-STAGE:sam:dme:AdaptorHostFcIfResetFcPersBinding:ExecutePeer) | warning | execute-peer-failed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 16534 | fsmStFailAdaptorHostFcIfResetFcPersBindingExecutePeer
F16535 | fsmStFailComputeBladeDiag:BiosPostCompletion | [FSM:STAGE:FAILED¦RETRY]: Waiting for BIOS POST completion from CIMC on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:BiosPostCompletion) | warning | bios-post-completion-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagBiosPostCompletion
F16535 | fsmStFailComputeBladeDiag:BladeBoot | [FSM:STAGE:FAILED¦RETRY]: Power-on server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:BladeBoot) | warning | blade-boot-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagBladeBoot
F16535 | fsmStFailComputeBladeDiag:BladeBootWait | [FSM:STAGE:FAILED¦RETRY]: Waiting for system reset on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:BladeBootWait) | warning | blade-boot-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagBladeBootWait
F16535 | fsmStFailComputeBladeDiag:BladePowerOn | [FSM:STAGE:FAILED¦RETRY]: Power on server [chassisId]/[slotId] for diagnostics(FSM-STAGE:sam:dme:ComputeBladeDiag:BladePowerOn) | warning | blade-power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagBladePowerOn
F16535 | fsmStFailComputeBladeDiag:BladeReadSmbios | [FSM:STAGE:FAILED¦RETRY]: Read SMBIOS tables on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:BladeReadSmbios) | warning | blade-read-smbios-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagBladeReadSmbios
F16535 | fsmStFailComputeBladeDiag:BmcConfigPnuOS | [FSM:STAGE:FAILED¦RETRY]: provisioning a bootable device with a bootable pre-boot image for server(FSM-STAGE:sam:dme:ComputeBladeDiag:BmcConfigPnuOS) | warning | bmc-config-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagBmcConfigPnuOS
F16535 | fsmStFailComputeBladeDiag:BmcInventory | [FSM:STAGE:FAILED¦RETRY]: Getting inventory of server [chassisId]/[slotId] via CIMC(FSM-STAGE:sam:dme:ComputeBladeDiag:BmcInventory) | warning | bmc-inventory-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagBmcInventory
F16535 | fsmStFailComputeBladeDiag:BmcPresence | [FSM:STAGE:FAILED¦RETRY]: Checking CIMC of server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:BmcPresence) | warning | bmc-presence-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagBmcPresence
F16535 | fsmStFailComputeBladeDiag:BmcShutdownDiagCompleted | [FSM:STAGE:FAILED¦RETRY]: Shutdown server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:BmcShutdownDiagCompleted) | warning | bmc-shutdown-diag-completed-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagBmcShutdownDiagCompleted
F16535 | fsmStFailComputeBladeDiag:CleanupServerConnSwA | [FSM:STAGE:FAILED¦RETRY]: Cleaning up server [chassisId]/[slotId] interface on fabric A(FSM-STAGE:sam:dme:ComputeBladeDiag:CleanupServerConnSwA) | warning | cleanup-server-conn-sw-afailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagCleanupServerConnSwA
F16535 | fsmStFailComputeBladeDiag:CleanupServerConnSwB | [FSM:STAGE:FAILED¦RETRY]: Cleaning up server [chassisId]/[slotId] interface on fabric B(FSM-STAGE:sam:dme:ComputeBladeDiag:CleanupServerConnSwB) | warning | cleanup-server-conn-sw-bfailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagCleanupServerConnSwB
F16535 | fsmStFailComputeBladeDiag:ConfigFeLocal | [FSM:STAGE:FAILED¦RETRY]: Configuring primary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:ConfigFeLocal) | warning | config-fe-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagConfigFeLocal
F16535 | fsmStFailComputeBladeDiag:ConfigFePeer | [FSM:STAGE:FAILED¦RETRY]: Configuring secondary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:ConfigFePeer) | warning | config-fe-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagConfigFePeer
F16535 | fsmStFailComputeBladeDiag:ConfigUserAccess | [FSM:STAGE:FAILED¦RETRY]: Configuring external user access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:ConfigUserAccess) | warning | config-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagConfigUserAccess
F16535 | fsmStFailComputeBladeDiag:DebugWait | [FSM:STAGE:FAILED¦RETRY]: Waiting for debugging for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:DebugWait) | warning | debug-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagDebugWait
F16535 | fsmStFailComputeBladeDiag:DeriveConfig | [FSM:STAGE:FAILED¦RETRY]: Derive diag config for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:DeriveConfig) | warning | derive-config-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagDeriveConfig
F16535 | fsmStFailComputeBladeDiag:DisableServerConnSwA | [FSM:STAGE:FAILED¦RETRY]: Disable server [chassisId]/[slotId] interface on fabric A after completion of network traffic tests on fabric A(FSM-STAGE:sam:dme:ComputeBladeDiag:DisableServerConnSwA) | warning | disable-server-conn-sw-afailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagDisableServerConnSwA
F16535 | fsmStFailComputeBladeDiag:DisableServerConnSwB | [FSM:STAGE:FAILED¦RETRY]: Disable server [chassisId]/[slotId] connectivity on fabric B in preparation for network traffic tests on fabric A(FSM-STAGE:sam:dme:ComputeBladeDiag:DisableServerConnSwB) | warning | disable-server-conn-sw-bfailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagDisableServerConnSwB
F16535 | fsmStFailComputeBladeDiag:EnableServerConnSwA | [FSM:STAGE:FAILED¦RETRY]: Enable server [chassisId]/[slotId] connectivity on fabric A in preparation for network traffic tests on fabric A(FSM-STAGE:sam:dme:ComputeBladeDiag:EnableServerConnSwA) | warning | enable-server-conn-sw-afailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagEnableServerConnSwA
F16535 | fsmStFailComputeBladeDiag:EnableServerConnSwB | [FSM:STAGE:FAILED¦RETRY]: Enable server [chassisId]/[slotId] connectivity on fabric B in preparation for network traffic tests on fabric B(FSM-STAGE:sam:dme:ComputeBladeDiag:EnableServerConnSwB) | warning | enable-server-conn-sw-bfailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagEnableServerConnSwB
F16535 | fsmStFailComputeBladeDiag:EvaluateStatus | [FSM:STAGE:FAILED¦RETRY]: Evaluating status; diagnostics completed(FSM-STAGE:sam:dme:ComputeBladeDiag:EvaluateStatus) | warning | evaluate-status-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagEvaluateStatus
F16535 | fsmStFailComputeBladeDiag:FabricATrafficTestStatus | [FSM:STAGE:FAILED¦RETRY]: Gather status of network traffic tests on fabric A for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:FabricATrafficTestStatus) | warning | fabricatraffic-test-status-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagFabricATrafficTestStatus
F16535 | fsmStFailComputeBladeDiag:FabricBTrafficTestStatus | [FSM:STAGE:FAILED¦RETRY]: Gather status of network tests on fabric B for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:FabricBTrafficTestStatus) | warning | fabricbtraffic-test-status-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagFabricBTrafficTestStatus
F16535 | fsmStFailComputeBladeDiag:GenerateLogWait | [FSM:STAGE:FAILED¦RETRY]: Waiting for collection of diagnostic logs from server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:GenerateLogWait) | warning | generate-log-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagGenerateLogWait
F16535 | fsmStFailComputeBladeDiag:GenerateReport | [FSM:STAGE:FAILED¦RETRY]: Generating report for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:GenerateReport) | warning | generate-report-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagGenerateReport
F16535 | fsmStFailComputeBladeDiag:HostCatalog | [FSM:STAGE:FAILED¦RETRY]: Populate diagnostics catalog to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostCatalog) | warning | host-catalog-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagHostCatalog
F16535 | fsmStFailComputeBladeDiag:HostConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to diagnostics environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostConnect) | warning | host-connect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagHostConnect
F16535 | fsmStFailComputeBladeDiag:HostDisconnect | [FSM:STAGE:FAILED¦RETRY]: Disconnect diagnostics environment agent for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostDisconnect) | warning | host-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagHostDisconnect
F16535 | fsmStFailComputeBladeDiag:HostIdent | [FSM:STAGE:FAILED¦RETRY]: Identify diagnostics environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostIdent) | warning | host-ident-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagHostIdent
F16535 | fsmStFailComputeBladeDiag:HostInventory | [FSM:STAGE:FAILED¦RETRY]: Perform inventory of server [chassisId]/[slotId] in diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:HostInventory) | warning | host-inventory-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagHostInventory
F16535 | fsmStFailComputeBladeDiag:HostPolicy | [FSM:STAGE:FAILED¦RETRY]: Populate diagnostics environment behavior policy to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostPolicy) | warning | host-policy-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagHostPolicy
F16535 | fsmStFailComputeBladeDiag:HostServerDiag | [FSM:STAGE:FAILED¦RETRY]: Trigger diagnostics on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostServerDiag) | warning | host-server-diag-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagHostServerDiag
F16535 | fsmStFailComputeBladeDiag:HostServerDiagStatus | [FSM:STAGE:FAILED¦RETRY]: Diagnostics status on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostServerDiagStatus) | warning | host-server-diag-status-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagHostServerDiagStatus
F16535 | fsmStFailComputeBladeDiag:NicConfigLocal | [FSM:STAGE:FAILED¦RETRY]: Configure adapter in server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:NicConfigLocal) | warning | nic-config-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagNicConfigLocal
F16535 | fsmStFailComputeBladeDiag:NicConfigPeer | [FSM:STAGE:FAILED¦RETRY]: Configure adapter in server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:NicConfigPeer) | warning | nic-config-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagNicConfigPeer
F16535 | fsmStFailComputeBladeDiag:NicInventoryLocal | [FSM:STAGE:FAILED¦RETRY]: Retrieve adapter inventory in server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:NicInventoryLocal) | warning | nic-inventory-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagNicInventoryLocal
F16535 | fsmStFailComputeBladeDiag:NicInventoryPeer | [FSM:STAGE:FAILED¦RETRY]: Retrieve adapter inventory in server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:NicInventoryPeer) | warning | nic-inventory-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagNicInventoryPeer
F16535 | fsmStFailComputeBladeDiag:NicPresenceLocal | [FSM:STAGE:FAILED¦RETRY]: Detect adapter in server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:NicPresenceLocal) | warning | nic-presence-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagNicPresenceLocal
F16535 | fsmStFailComputeBladeDiag:NicPresencePeer | [FSM:STAGE:FAILED¦RETRY]: Detect adapter in server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:NicPresencePeer) | warning | nic-presence-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagNicPresencePeer
F16535 | fsmStFailComputeBladeDiag:NicUnconfigLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfigure adapter of server [chassisId]/[slotId] diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:NicUnconfigLocal) | warning | nic-unconfig-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagNicUnconfigLocal
F16535 | fsmStFailComputeBladeDiag:NicUnconfigPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfigure adapter of server [chassisId]/[slotId] diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:NicUnconfigPeer) | warning | nic-unconfig-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagNicUnconfigPeer
F16535 | fsmStFailComputeBladeDiag:RemoveConfig | [FSM:STAGE:FAILED¦RETRY]: Derive diag config for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:RemoveConfig) | warning | remove-config-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagRemoveConfig
F16535 | fsmStFailComputeBladeDiag:RemoveVMediaLocal | [FSM:STAGE:FAILED¦RETRY]: Remove VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:RemoveVMediaLocal) | warning | removevmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagRemoveVMediaLocal
F16535 | fsmStFailComputeBladeDiag:RemoveVMediaPeer | [FSM:STAGE:FAILED¦RETRY]: Remove VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:RemoveVMediaPeer) | warning | removevmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagRemoveVMediaPeer
F16535 | fsmStFailComputeBladeDiag:RestoreConfigFeLocal | [FSM:STAGE:FAILED¦RETRY]: Reconfiguring primary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:RestoreConfigFeLocal) | warning | restore-config-fe-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagRestoreConfigFeLocal
F16535 | fsmStFailComputeBladeDiag:RestoreConfigFePeer | [FSM:STAGE:FAILED¦RETRY]: Reconfiguring secondary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:RestoreConfigFePeer) | warning | restore-config-fe-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagRestoreConfigFePeer
F16535 | fsmStFailComputeBladeDiag:SetDiagUser | [FSM:STAGE:FAILED¦RETRY]: Populate diagnostics environment with a user account to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:SetDiagUser) | warning | set-diag-user-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSetDiagUser
F16535 | fsmStFailComputeBladeDiag:SetupVMediaLocal | [FSM:STAGE:FAILED¦RETRY]: Setup VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SetupVMediaLocal) | warning | setupvmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSetupVMediaLocal
F16535 | fsmStFailComputeBladeDiag:SetupVMediaPeer | [FSM:STAGE:FAILED¦RETRY]: Setup VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SetupVMediaPeer) | warning | setupvmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSetupVMediaPeer
F16535 | fsmStFailComputeBladeDiag:SolRedirectDisable | [FSM:STAGE:FAILED¦RETRY]: Disable Sol Redirection on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:SolRedirectDisable) | warning | sol-redirect-disable-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSolRedirectDisable
F16535 | fsmStFailComputeBladeDiag:SolRedirectEnable | [FSM:STAGE:FAILED¦RETRY]: set up bios token on server [chassisId]/[slotId] for Sol redirect(FSM-STAGE:sam:dme:ComputeBladeDiag:SolRedirectEnable) | warning | sol-redirect-enable-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSolRedirectEnable
F16535 | fsmStFailComputeBladeDiag:StartFabricATrafficTest | [FSM:STAGE:FAILED¦RETRY]: Trigger network traffic tests on fabric A on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:StartFabricATrafficTest) | warning | start-fabricatraffic-test-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagStartFabricATrafficTest
F16535 | fsmStFailComputeBladeDiag:StartFabricBTrafficTest | [FSM:STAGE:FAILED¦RETRY]: Trigger network tests on fabric B for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:StartFabricBTrafficTest) | warning | start-fabricbtraffic-test-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagStartFabricBTrafficTest
F16535 | fsmStFailComputeBladeDiag:StopVMediaLocal | [FSM:STAGE:FAILED¦RETRY]: Stop VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:StopVMediaLocal) | warning | stopvmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagStopVMediaLocal
F16535 | fsmStFailComputeBladeDiag:StopVMediaPeer | [FSM:STAGE:FAILED¦RETRY]: Stop VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:StopVMediaPeer) | warning | stopvmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagStopVMediaPeer
F16535 | fsmStFailComputeBladeDiag:SwConfigLocal | [FSM:STAGE:FAILED¦RETRY]: Configure primary fabric interconnect in server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SwConfigLocal) | warning | sw-config-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSwConfigLocal
F16535 | fsmStFailComputeBladeDiag:SwConfigPeer | [FSM:STAGE:FAILED¦RETRY]: Configure secondary fabric interconnect in server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SwConfigPeer) | warning | sw-config-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSwConfigPeer
F16535 | fsmStFailComputeBladeDiag:SwUnconfigLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfigure primary fabric interconnect for server [chassisId]/[slotId] in diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SwUnconfigLocal) | warning | sw-unconfig-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSwUnconfigLocal
F16535 | fsmStFailComputeBladeDiag:SwUnconfigPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfigure secondary fabric interconnect for server [chassisId]/[slotId] in diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SwUnconfigPeer) | warning | sw-unconfig-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSwUnconfigPeer
F16535 | fsmStFailComputeBladeDiag:UnconfigUserAccess | [FSM:STAGE:FAILED¦RETRY]: Unconfigure external user access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:UnconfigUserAccess) | warning | unconfig-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagUnconfigUserAccess
F16535 | fsmStFailComputeBladeDiag:serialDebugConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to pre-boot environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:serialDebugConnect) | warning | serial-debug-connect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSerialDebugConnect
F16535 | fsmStFailComputeBladeDiag:serialDebugDisconnect | [FSM:STAGE:FAILED¦RETRY]: Disconnect pre-boot environment agent for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:serialDebugDisconnect) | warning | serial-debug-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16535 | fsmStFailComputeBladeDiagSerialDebugDisconnect
F16539 | fsmStFailFabricLanCloudSwitchMode:SwConfigLocal | [FSM:STAGE:FAILED¦RETRY]: (FSM-STAGE:sam:dme:FabricLanCloudSwitchMode:SwConfigLocal) | warning | sw-config-local-failed | None set. | None set. | none | TRUE | fsm | fabric:LanCloud | fabric/lan | 16539 | fsmStFailFabricLanCloudSwitchModeSwConfigLocal
F16539 | fsmStFailFabricLanCloudSwitchMode:SwConfigPeer | [FSM:STAGE:FAILED¦RETRY]: Fabric interconnect mode configuration to primary(FSM-STAGE:sam:dme:FabricLanCloudSwitchMode:SwConfigPeer) | warning | sw-config-peer-failed | None set. | None set. | none | TRUE | fsm | fabric:LanCloud | fabric/lan | 16539 | fsmStFailFabricLanCloudSwitchModeSwConfigPeer
F16539 | fsmStFailFabricSanCloudSwitchMode:SwConfigLocal | [FSM:STAGE:FAILED¦RETRY]: (FSM-STAGE:sam:dme:FabricSanCloudSwitchMode:SwConfigLocal) | warning | sw-config-local-failed | None set. | None set. | none | TRUE | fsm | fabric:SanCloud | fabric/san | 16539 | fsmStFailFabricSanCloudSwitchModeSwConfigLocal
F16539 | fsmStFailFabricSanCloudSwitchMode:SwConfigPeer | [FSM:STAGE:FAILED¦RETRY]: Fabric interconnect FC mode configuration to primary(FSM-STAGE:sam:dme:FabricSanCloudSwitchMode:SwConfigPeer) | warning | sw-config-peer-failed | None set. | None set. | none | TRUE | fsm | fabric:SanCloud | fabric/san | 16539 | fsmStFailFabricSanCloudSwitchModeSwConfigPeer
F16576 | fsmStFailCommSvcEpUpdateSvcEp:PropogateEpSettings | [FSM:STAGE:FAILED¦RETRY]: propogate updated settings (eg. timezone)(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpSettings) | warning | propogate-ep-settings-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16576 | fsmStFailCommSvcEpUpdateSvcEpPropogateEpSettings
F16576 | fsmStFailCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsLocal | [FSM:STAGE:FAILED¦RETRY]: propogate updated timezone settings to management controllers.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsLocal) | warning | propogate-ep-time-zone-settings-local-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16576 | fsmStFailCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsLocal
F16576 | fsmStFailCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsPeer | [FSM:STAGE:FAILED¦RETRY]: propogate updated timezone settings to management controllers.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsPeer) | warning | propogate-ep-time-zone-settings-peer-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16576 | fsmStFailCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsPeer
F16576 | fsmStFailCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToAdaptorsLocal | [FSM:STAGE:FAILED¦RETRY]: propogate updated timezone settings to NICs.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToAdaptorsLocal) | warning | propogate-ep-time-zone-settings-to-adaptors-local-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16576 | fsmStFailCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsToAdaptorsLocal
F16576 | fsmStFailCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToAdaptorsPeer | [FSM:STAGE:FAILED¦RETRY]: propogate updated timezone settings to NICs.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToAdaptorsPeer) | warning | propogate-ep-time-zone-settings-to-adaptors-peer-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16576 | fsmStFailCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsToAdaptorsPeer
F16576 | fsmStFailCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToFexIomLocal | [FSM:STAGE:FAILED¦RETRY]: propogate updated timezone settings to FEXs and IOMs.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToFexIomLocal) | warning | propogate-ep-time-zone-settings-to-fex-iom-local-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16576 | fsmStFailCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsToFexIomLocal
F16576 | fsmStFailCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToFexIomPeer | [FSM:STAGE:FAILED¦RETRY]: propogate updated timezone settings to FEXs and IOMs.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToFexIomPeer) | warning | propogate-ep-time-zone-settings-to-fex-iom-peer-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16576 | fsmStFailCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsToFexIomPeer
F16576 | fsmStFailCommSvcEpUpdateSvcEp:SetEpLocal | [FSM:STAGE:FAILED¦RETRY]: communication service [name] configuration to primary(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:SetEpLocal) | warning | set-ep-local-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16576 | fsmStFailCommSvcEpUpdateSvcEpSetEpLocal
F16576 | fsmStFailCommSvcEpUpdateSvcEp:SetEpPeer | [FSM:STAGE:FAILED¦RETRY]: communication service [name] configuration to secondary(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:SetEpPeer) | warning | set-ep-peer-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16576 | fsmStFailCommSvcEpUpdateSvcEpSetEpPeer
F16577 | fsmStFailCommSvcEpRestartWebSvc:local | [FSM:STAGE:FAILED¦RETRY]: restart web services in primary(FSM-STAGE:sam:dme:CommSvcEpRestartWebSvc:local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16577 | fsmStFailCommSvcEpRestartWebSvcLocal
F16577 | fsmStFailCommSvcEpRestartWebSvc:peer | [FSM:STAGE:FAILED¦RETRY]: restart web services in secondary(FSM-STAGE:sam:dme:CommSvcEpRestartWebSvc:peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 16577 | fsmStFailCommSvcEpRestartWebSvcPeer
F16579 | fsmStFailAaaEpUpdateEp:SetEpLocal | [FSM:STAGE:FAILED¦RETRY]: external aaa server configuration to primary(FSM-STAGE:sam:dme:AaaEpUpdateEp:SetEpLocal) | warning | set-ep-local-failed | None set. | None set. | none | TRUE | fsm | aaa:Ep | sys/ | 16579 | fsmStFailAaaEpUpdateEpSetEpLocal
F16579 | fsmStFailAaaEpUpdateEp:SetEpPeer | [FSM:STAGE:FAILED¦RETRY]: external aaa server configuration to secondary(FSM-STAGE:sam:dme:AaaEpUpdateEp:SetEpPeer) | warning | set-ep-peer-failed | None set. | None set. | none | TRUE | fsm | aaa:Ep | sys/ | 16579 | fsmStFailAaaEpUpdateEpSetEpPeer
F16579 | fsmStFailPkiEpUpdateEp:SetKeyRingLocal | [FSM:STAGE:FAILED¦RETRY]: keyring configuration on primary(FSM-STAGE:sam:dme:PkiEpUpdateEp:SetKeyRingLocal) | warning | set-key-ring-local-failed | None set. | None set. | none | TRUE | fsm | pki:Ep | sys/pki-ext | 16579 | fsmStFailPkiEpUpdateEpSetKeyRingLocal
F16579 | fsmStFailPkiEpUpdateEp:SetKeyRingPeer | [FSM:STAGE:FAILED¦RETRY]: keyring configuration on secondary(FSM-STAGE:sam:dme:PkiEpUpdateEp:SetKeyRingPeer) | warning | set-key-ring-peer-failed | None set. | None set. | none | TRUE | fsm | pki:Ep | sys/pki-ext | 16579 | fsmStFailPkiEpUpdateEpSetKeyRingPeer
F16579 | fsmStFailStatsCollectionPolicyUpdateEp:SetEpA | [FSM:STAGE:FAILED¦RETRY]: Update endpoint on fabric interconnect A(FSM-STAGE:sam:dme:StatsCollectionPolicyUpdateEp:SetEpA) | warning | set-ep-afailed | None set. | None set. | none | TRUE | fsm | stats:CollectionPolicy | stats/coll-policy-[name] | 16579 | fsmStFailStatsCollectionPolicyUpdateEpSetEpA
F16579 | fsmStFailStatsCollectionPolicyUpdateEp:SetEpB | [FSM:STAGE:FAILED¦RETRY]: Update endpoint on fabric interconnect B(FSM-STAGE:sam:dme:StatsCollectionPolicyUpdateEp:SetEpB) | warning | set-ep-bfailed | None set. | None set. | none | TRUE | fsm | stats:CollectionPolicy | stats/coll-policy-[name] | 16579 | fsmStFailStatsCollectionPolicyUpdateEpSetEpB
F16580 | fsmStFailAaaRealmUpdateRealm:SetRealmLocal | [FSM:STAGE:FAILED¦RETRY]: realm configuration to primary(FSM-STAGE:sam:dme:AaaRealmUpdateRealm:SetRealmLocal) | warning | set-realm-local-failed | None set. | None set. | none | TRUE | fsm | aaa:Realm | sys/ | 16580 | fsmStFailAaaRealmUpdateRealmSetRealmLocal
F16580 | fsmStFailAaaRealmUpdateRealm:SetRealmPeer | [FSM:STAGE:FAILED¦RETRY]: realm configuration to secondary(FSM-STAGE:sam:dme:AaaRealmUpdateRealm:SetRealmPeer) | warning | set-realm-peer-failed | None set. | None set. | none | TRUE | fsm | aaa:Realm | sys/ | 16580 | fsmStFailAaaRealmUpdateRealmSetRealmPeer
F16581 | fsmStFailAaaUserEpUpdateUserEp:SetUserLocal | [FSM:STAGE:FAILED¦RETRY]: user configuration to primary(FSM-STAGE:sam:dme:AaaUserEpUpdateUserEp:SetUserLocal) | warning | set-user-local-failed | None set. | None set. | none | TRUE | fsm | aaa:UserEp | sys/user-ext | 16581 | fsmStFailAaaUserEpUpdateUserEpSetUserLocal
F16581 | fsmStFailAaaUserEpUpdateUserEp:SetUserPeer | [FSM:STAGE:FAILED¦RETRY]: user configuration to secondary(FSM-STAGE:sam:dme:AaaUserEpUpdateUserEp:SetUserPeer) | warning | set-user-peer-failed | None set. | None set. | none | TRUE | fsm | aaa:UserEp | sys/user-ext | 16581 | fsmStFailAaaUserEpUpdateUserEpSetUserPeer
F16600 | fsmStFailSysfileMutationSingle:Execute | [FSM:STAGE:FAILED¦RETRY]: [action] file [name](FSM-STAGE:sam:dme:SysfileMutationSingle:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | sysfile:Mutation | sys/corefiles/file-[name]¦[switchId]/mutation | 16600 | fsmStFailSysfileMutationSingleExecute
F16601 | fsmStFailSysfileMutationGlobal:Local | [FSM:STAGE:FAILED¦RETRY]: remove files from local(FSM-STAGE:sam:dme:SysfileMutationGlobal:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | sysfile:Mutation | sys/corefiles/file-[name]¦[switchId]/mutation | 16601 | fsmStFailSysfileMutationGlobalLocal
F16601 | fsmStFailSysfileMutationGlobal:Peer | [FSM:STAGE:FAILED¦RETRY]: remove files from peer(FSM-STAGE:sam:dme:SysfileMutationGlobal:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | sysfile:Mutation | sys/corefiles/file-[name]¦[switchId]/mutation | 16601 | fsmStFailSysfileMutationGlobalPeer
F16604 | fsmStFailSysdebugManualCoreFileExportTargetExport:Execute | [FSM:STAGE:FAILED¦RETRY]: export core file [name] to [hostname](FSM-STAGE:sam:dme:SysdebugManualCoreFileExportTargetExport:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | sysdebug:ManualCoreFileExportTarget | sys/corefiles/file-[name]¦[switchId]/export-to-[hostname] | 16604 | fsmStFailSysdebugManualCoreFileExportTargetExportExecute
F16605 | fsmStFailFabricEpMgrConfigure:ApplyConfig | [FSM:STAGE:FAILED¦RETRY]: Apply switch configuration(FSM-STAGE:sam:dme:FabricEpMgrConfigure:ApplyConfig) | warning | apply-config-failed | None set. | None set. | none | TRUE | fsm | fabric:EpMgr | fabric/[id] | 16605 | fsmStFailFabricEpMgrConfigureApplyConfig
F16605 | fsmStFailFabricEpMgrConfigure:ApplyPhysical | [FSM:STAGE:FAILED¦RETRY]: Applying physical configuration(FSM-STAGE:sam:dme:FabricEpMgrConfigure:ApplyPhysical) | warning | apply-physical-failed | None set. | None set. | none | TRUE | fsm | fabric:EpMgr | fabric/[id] | 16605 | fsmStFailFabricEpMgrConfigureApplyPhysical
F16605 | fsmStFailFabricEpMgrConfigure:ValidateConfiguration | [FSM:STAGE:FAILED¦RETRY]: Validating logical configuration(FSM-STAGE:sam:dme:FabricEpMgrConfigure:ValidateConfiguration) | warning | validate-configuration-failed | None set. | None set. | none | TRUE | fsm | fabric:EpMgr | fabric/[id] | 16605 | fsmStFailFabricEpMgrConfigureValidateConfiguration
F16605 | fsmStFailFabricEpMgrConfigure:WaitOnPhys | [FSM:STAGE:FAILED¦RETRY]: Waiting on physical change application(FSM-STAGE:sam:dme:FabricEpMgrConfigure:WaitOnPhys) | warning | wait-on-phys-failed | None set. | None set. | none | TRUE | fsm | fabric:EpMgr | fabric/[id] | 16605 | fsmStFailFabricEpMgrConfigureWaitOnPhys
F16605 | fsmStFailLsServerConfigure:AnalyzeImpact | [FSM:STAGE:FAILED¦RETRY]: Analyzing changes impact(FSM-STAGE:sam:dme:LsServerConfigure:AnalyzeImpact) | warning | analyze-impact-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 16605 | fsmStFailLsServerConfigureAnalyzeImpact
F16605 | fsmStFailLsServerConfigure:ApplyConfig | [FSM:STAGE:FAILED¦RETRY]: Applying config to server [pnDn](FSM-STAGE:sam:dme:LsServerConfigure:ApplyConfig) | warning | apply-config-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 16605 | fsmStFailLsServerConfigureApplyConfig
F16605 | fsmStFailLsServerConfigure:ApplyIdentifiers | [FSM:STAGE:FAILED¦RETRY]: Resolving and applying identifiers(FSM-STAGE:sam:dme:LsServerConfigure:ApplyIdentifiers) | warning | apply-identifiers-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 16605 | fsmStFailLsServerConfigureApplyIdentifiers
F16605 | fsmStFailLsServerConfigure:ApplyPolicies | [FSM:STAGE:FAILED¦RETRY]: Resolving and applying policies(FSM-STAGE:sam:dme:LsServerConfigure:ApplyPolicies) | warning | apply-policies-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 16605 | fsmStFailLsServerConfigureApplyPolicies
F16605 | fsmStFailLsServerConfigure:ApplyTemplate | [FSM:STAGE:FAILED¦RETRY]: Applying configuration template [srcTemplName](FSM-STAGE:sam:dme:LsServerConfigure:ApplyTemplate) | warning | apply-template-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 16605 | fsmStFailLsServerConfigureApplyTemplate
F16605 | fsmStFailLsServerConfigure:EvaluateAssociation | [FSM:STAGE:FAILED¦RETRY]: Evaluate association with server [pnDn](FSM-STAGE:sam:dme:LsServerConfigure:EvaluateAssociation) | warning | evaluate-association-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 16605 | fsmStFailLsServerConfigureEvaluateAssociation
F16605 | fsmStFailLsServerConfigure:ResolveBootConfig | [FSM:STAGE:FAILED¦RETRY]: Computing binding changes(FSM-STAGE:sam:dme:LsServerConfigure:ResolveBootConfig) | warning | resolve-boot-config-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 16605 | fsmStFailLsServerConfigureResolveBootConfig
F16605 | fsmStFailLsServerConfigure:WaitForMaintPermission | [FSM:STAGE:FAILED¦RETRY]: Waiting for ack or maint window(FSM-STAGE:sam:dme:LsServerConfigure:WaitForMaintPermission) | warning | wait-for-maint-permission-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 16605 | fsmStFailLsServerConfigureWaitForMaintPermission
F16605 | fsmStFailLsServerConfigure:WaitForMaintWindow | [FSM:STAGE:FAILED¦RETRY]: Waiting for maintenance window(FSM-STAGE:sam:dme:LsServerConfigure:WaitForMaintWindow) | warning | wait-for-maint-window-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 16605 | fsmStFailLsServerConfigureWaitForMaintWindow
F16605 | fsmStFailSysdebugAutoCoreFileExportTargetConfigure:Local | [FSM:STAGE:FAILED¦RETRY]: configuring automatic core file export service on local(FSM-STAGE:sam:dme:SysdebugAutoCoreFileExportTargetConfigure:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | sysdebug:AutoCoreFileExportTarget | sys/sysdebug/file-export | 16605 | fsmStFailSysdebugAutoCoreFileExportTargetConfigureLocal
F16605 | fsmStFailSysdebugAutoCoreFileExportTargetConfigure:Peer | [FSM:STAGE:FAILED¦RETRY]: configuring automatic core file export service on peer(FSM-STAGE:sam:dme:SysdebugAutoCoreFileExportTargetConfigure:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | sysdebug:AutoCoreFileExportTarget | sys/sysdebug/file-export | 16605 | fsmStFailSysdebugAutoCoreFileExportTargetConfigurePeer
F16606 | fsmStFailSysdebugLogControlEpLogControlPersist:Local | [FSM:STAGE:FAILED¦RETRY]: persisting LogControl on local(FSM-STAGE:sam:dme:SysdebugLogControlEpLogControlPersist:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | sysdebug:LogControlEp | sys/sysdebug/logcontrol | 16606 | fsmStFailSysdebugLogControlEpLogControlPersistLocal
F16606 | fsmStFailSysdebugLogControlEpLogControlPersist:Peer | [FSM:STAGE:FAILED¦RETRY]: persisting LogControl on peer(FSM-STAGE:sam:dme:SysdebugLogControlEpLogControlPersist:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | sysdebug:LogControlEp | sys/sysdebug/logcontrol | 16606 | fsmStFailSysdebugLogControlEpLogControlPersistPeer
F16634 | fsmStFailEpqosDefinitionDeploy:Local | [FSM:STAGE:FAILED¦RETRY]: vnic qos policy [name] configuration to primary(FSM-STAGE:sam:dme:EpqosDefinitionDeploy:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | epqos:Definition | org-[name]/ep-qos-[name] | 16634 | fsmStFailEpqosDefinitionDeployLocal
F16634 | fsmStFailEpqosDefinitionDeploy:Peer | [FSM:STAGE:FAILED¦RETRY]: vnic qos policy [name] configuration to secondary(FSM-STAGE:sam:dme:EpqosDefinitionDeploy:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | epqos:Definition | org-[name]/ep-qos-[name] | 16634 | fsmStFailEpqosDefinitionDeployPeer
F16634 | fsmStFailSwAccessDomainDeploy:UpdateConnectivity | [FSM:STAGE:FAILED¦RETRY]: internal network configuration on [switchId](FSM-STAGE:sam:dme:SwAccessDomainDeploy:UpdateConnectivity) | warning | update-connectivity-failed | None set. | None set. | none | TRUE | fsm | sw:AccessDomain | sys/switch-[id]/access-eth | 16634 | fsmStFailSwAccessDomainDeployUpdateConnectivity
F16634 | fsmStFailSwEthLanBorderDeploy:UpdateConnectivity | [FSM:STAGE:FAILED¦RETRY]: Uplink eth port configuration on [switchId](FSM-STAGE:sam:dme:SwEthLanBorderDeploy:UpdateConnectivity) | warning | update-connectivity-failed | None set. | None set. | none | TRUE | fsm | sw:EthLanBorder | sys/switch-[id]/border-eth | 16634 | fsmStFailSwEthLanBorderDeployUpdateConnectivity
F16634 | fsmStFailSwEthMonDeploy:UpdateEthMon | [FSM:STAGE:FAILED¦RETRY]: Ethernet traffic monitor (SPAN)configuration on [switchId](FSM-STAGE:sam:dme:SwEthMonDeploy:UpdateEthMon) | warning | update-eth-mon-failed | None set. | None set. | none | TRUE | fsm | sw:EthMon | sys/switch-[id]/lanmon-eth/mon-[name] | 16634 | fsmStFailSwEthMonDeployUpdateEthMon
F16634 | fsmStFailSwFcMonDeploy:UpdateFcMon | [FSM:STAGE:FAILED¦RETRY]: FC traffic monitor (SPAN)configuration on [switchId](FSM-STAGE:sam:dme:SwFcMonDeploy:UpdateFcMon) | warning | update-fc-mon-failed | None set. | None set. | none | TRUE | fsm | sw:FcMon | sys/switch-[id]/sanmon-fc/mon-[name] | 16634 | fsmStFailSwFcMonDeployUpdateFcMon
F16634 | fsmStFailSwFcSanBorderDeploy:UpdateConnectivity | [FSM:STAGE:FAILED¦RETRY]: Uplink fc port configuration on [switchId](FSM-STAGE:sam:dme:SwFcSanBorderDeploy:UpdateConnectivity) | warning | update-connectivity-failed | None set. | None set. | none | TRUE | fsm | sw:FcSanBorder | sys/switch-[id]/border-fc | 16634 | fsmStFailSwFcSanBorderDeployUpdateConnectivity
F16634 | fsmStFailSwUtilityDomainDeploy:UpdateConnectivity | [FSM:STAGE:FAILED¦RETRY]: Utility network configuration on [switchId](FSM-STAGE:sam:dme:SwUtilityDomainDeploy:UpdateConnectivity) | warning | update-connectivity-failed | None set. | None set. | none | TRUE | fsm | sw:UtilityDomain | sys/switch-[id]/utility-eth | 16634 | fsmStFailSwUtilityDomainDeployUpdateConnectivity
F16634 | fsmStFailVnicProfileSetDeploy:Local | [FSM:STAGE:FAILED¦RETRY]: VNIC profile configuration on local fabric(FSM-STAGE:sam:dme:VnicProfileSetDeploy:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | vnic:ProfileSet | fabric/lan/profiles | 16634 | fsmStFailVnicProfileSetDeployLocal
F16634 | fsmStFailVnicProfileSetDeploy:Peer | [FSM:STAGE:FAILED¦RETRY]: VNIC profile configuration on peer fabric(FSM-STAGE:sam:dme:VnicProfileSetDeploy:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | vnic:ProfileSet | fabric/lan/profiles | 16634 | fsmStFailVnicProfileSetDeployPeer
F16641 | fsmStFailSyntheticFsObjCreate:createLocal | [FSM:STAGE:FAILED¦RETRY]: create on primary(FSM-STAGE:sam:dme:SyntheticFsObjCreate:createLocal) | warning | create-local-failed | None set. | None set. | none | TRUE | fsm | synthetic:FsObj | sys/file-[name] | 16641 | fsmStFailSyntheticFsObjCreateCreateLocal
F16641 | fsmStFailSyntheticFsObjCreate:createRemote | [FSM:STAGE:FAILED¦RETRY]: create on secondary(FSM-STAGE:sam:dme:SyntheticFsObjCreate:createRemote) | warning | create-remote-failed | None set. | None set. | none | TRUE | fsm | synthetic:FsObj | sys/file-[name] | 16641 | fsmStFailSyntheticFsObjCreateCreateRemote
F16651 | fsmStFailFirmwareDistributableDelete:Local | [FSM:STAGE:FAILED¦RETRY]: deleting package [name] from primary(FSM-STAGE:sam:dme:FirmwareDistributableDelete:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | firmware:Distributable | sys/fw-catalogue/distrib-[name] | 16651 | fsmStFailFirmwareDistributableDeleteLocal
F16651 | fsmStFailFirmwareDistributableDelete:Remote | [FSM:STAGE:FAILED¦RETRY]: deleting package [name] from secondary(FSM-STAGE:sam:dme:FirmwareDistributableDelete:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | firmware:Distributable | sys/fw-catalogue/distrib-[name] | 16651 | fsmStFailFirmwareDistributableDeleteRemote
F16651 | fsmStFailFirmwareImageDelete:Local | [FSM:STAGE:FAILED¦RETRY]: deleting image file [name] ([invTag]) from primary(FSM-STAGE:sam:dme:FirmwareImageDelete:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | firmware:Image | sys/fw-catalogue/image-[name] | 16651 | fsmStFailFirmwareImageDeleteLocal
F16651 | fsmStFailFirmwareImageDelete:Remote | [FSM:STAGE:FAILED¦RETRY]: deleting image file [name] ([invTag]) from secondary(FSM-STAGE:sam:dme:FirmwareImageDelete:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | firmware:Image | sys/fw-catalogue/image-[name] | 16651 | fsmStFailFirmwareImageDeleteRemote
F16653 | fsmStFailMgmtControllerUpdateSwitch:resetLocal | [FSM:STAGE:FAILED¦RETRY]: rebooting local fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:resetLocal) | warning | reset-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16653 | fsmStFailMgmtControllerUpdateSwitchResetLocal
F16653 | fsmStFailMgmtControllerUpdateSwitch:resetRemote | [FSM:STAGE:FAILED¦RETRY]: rebooting remote fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:resetRemote) | warning | reset-remote-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16653 | fsmStFailMgmtControllerUpdateSwitchResetRemote
F16653 | fsmStFailMgmtControllerUpdateSwitch:updateLocal | [FSM:STAGE:FAILED¦RETRY]: updating local fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:updateLocal) | warning | update-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16653 | fsmStFailMgmtControllerUpdateSwitchUpdateLocal
F16653 | fsmStFailMgmtControllerUpdateSwitch:updateRemote | [FSM:STAGE:FAILED¦RETRY]: updating peer fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:updateRemote) | warning | update-remote-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16653 | fsmStFailMgmtControllerUpdateSwitchUpdateRemote
F16653 | fsmStFailMgmtControllerUpdateSwitch:verifyLocal | [FSM:STAGE:FAILED¦RETRY]: verifying boot variables for local fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:verifyLocal) | warning | verify-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16653 | fsmStFailMgmtControllerUpdateSwitchVerifyLocal
F16653 | fsmStFailMgmtControllerUpdateSwitch:verifyRemote | [FSM:STAGE:FAILED¦RETRY]: verifying boot variables for remote fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:verifyRemote) | warning | verify-remote-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16653 | fsmStFailMgmtControllerUpdateSwitchVerifyRemote
F16654 | fsmStFailMgmtControllerUpdateIOM:PollUpdateStatus | [FSM:STAGE:FAILED¦RETRY]: waiting for IOM update(FSM-STAGE:sam:dme:MgmtControllerUpdateIOM:PollUpdateStatus) | warning | poll-update-status-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16654 | fsmStFailMgmtControllerUpdateIOMPollUpdateStatus
F16654 | fsmStFailMgmtControllerUpdateIOM:UpdateRequest | [FSM:STAGE:FAILED¦RETRY]: sending update request to IOM(FSM-STAGE:sam:dme:MgmtControllerUpdateIOM:UpdateRequest) | warning | update-request-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16654 | fsmStFailMgmtControllerUpdateIOMUpdateRequest
F16655 | fsmStFailMgmtControllerActivateIOM:Activate | [FSM:STAGE:FAILED¦RETRY]: activating backup image of IOM(FSM-STAGE:sam:dme:MgmtControllerActivateIOM:Activate) | warning | activate-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16655 | fsmStFailMgmtControllerActivateIOMActivate
F16655 | fsmStFailMgmtControllerActivateIOM:Reset | [FSM:STAGE:FAILED¦RETRY]: Resetting IOM to boot the activated version(FSM-STAGE:sam:dme:MgmtControllerActivateIOM:Reset) | warning | reset-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16655 | fsmStFailMgmtControllerActivateIOMReset
F16656 | fsmStFailMgmtControllerUpdateBMC:PollUpdateStatus | [FSM:STAGE:FAILED¦RETRY]: waiting for update to complete(FSM-STAGE:sam:dme:MgmtControllerUpdateBMC:PollUpdateStatus) | warning | poll-update-status-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16656 | fsmStFailMgmtControllerUpdateBMCPollUpdateStatus
F16656 | fsmStFailMgmtControllerUpdateBMC:UpdateRequest | [FSM:STAGE:FAILED¦RETRY]: sending update request to CIMC(FSM-STAGE:sam:dme:MgmtControllerUpdateBMC:UpdateRequest) | warning | update-request-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16656 | fsmStFailMgmtControllerUpdateBMCUpdateRequest
F16657 | fsmStFailMgmtControllerActivateBMC:Activate | [FSM:STAGE:FAILED¦RETRY]: activating backup image of CIMC(FSM-STAGE:sam:dme:MgmtControllerActivateBMC:Activate) | warning | activate-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16657 | fsmStFailMgmtControllerActivateBMCActivate
F16657 | fsmStFailMgmtControllerActivateBMC:Reset | [FSM:STAGE:FAILED¦RETRY]: Resetting CIMC to boot the activated version(FSM-STAGE:sam:dme:MgmtControllerActivateBMC:Reset) | warning | reset-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16657 | fsmStFailMgmtControllerActivateBMCReset
F16670 | fsmStFailCallhomeEpConfigCallhome:SetLocal | [FSM:STAGE:FAILED¦RETRY]: call-home configuration on primary(FSM-STAGE:sam:dme:CallhomeEpConfigCallhome:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | callhome:Ep | call-home | 16670 | fsmStFailCallhomeEpConfigCallhomeSetLocal
F16670 | fsmStFailCallhomeEpConfigCallhome:SetPeer | [FSM:STAGE:FAILED¦RETRY]: call-home configuration on secondary(FSM-STAGE:sam:dme:CallhomeEpConfigCallhome:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | callhome:Ep | call-home | 16670 | fsmStFailCallhomeEpConfigCallhomeSetPeer
F16673 | fsmStFailMgmtIfSwMgmtOobIfConfig:Switch | [FSM:STAGE:FAILED¦RETRY]: configuring the out-of-band interface(FSM-STAGE:sam:dme:MgmtIfSwMgmtOobIfConfig:Switch) | warning | switch-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 16673 | fsmStFailMgmtIfSwMgmtOobIfConfigSwitch
F16674 | fsmStFailMgmtIfSwMgmtInbandIfConfig:Switch | [FSM:STAGE:FAILED¦RETRY]: configuring the inband interface(FSM-STAGE:sam:dme:MgmtIfSwMgmtInbandIfConfig:Switch) | warning | switch-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 16674 | fsmStFailMgmtIfSwMgmtInbandIfConfigSwitch
F16679 | fsmStFailMgmtIfVirtualIfConfig:Local | [FSM:STAGE:FAILED¦RETRY]: Updating virtual interface on local fabric interconnect(FSM-STAGE:sam:dme:MgmtIfVirtualIfConfig:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 16679 | fsmStFailMgmtIfVirtualIfConfigLocal
F16679 | fsmStFailMgmtIfVirtualIfConfig:Remote | [FSM:STAGE:FAILED¦RETRY]: Updating virtual interface on peer fabric interconnect(FSM-STAGE:sam:dme:MgmtIfVirtualIfConfig:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 16679 | fsmStFailMgmtIfVirtualIfConfigRemote
F16680 | fsmStFailMgmtIfEnableVip:Local | [FSM:STAGE:FAILED¦RETRY]: Enable virtual interface on local fabric interconnect(FSM-STAGE:sam:dme:MgmtIfEnableVip:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 16680 | fsmStFailMgmtIfEnableVipLocal
F16681 | fsmStFailMgmtIfDisableVip:Peer | [FSM:STAGE:FAILED¦RETRY]: Disable virtual interface on peer fabric interconnect(FSM-STAGE:sam:dme:MgmtIfDisableVip:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 16681 | fsmStFailMgmtIfDisableVipPeer
F16682 | fsmStFailMgmtIfEnableHA:Local | [FSM:STAGE:FAILED¦RETRY]: Transition from single to cluster mode(FSM-STAGE:sam:dme:MgmtIfEnableHA:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 16682 | fsmStFailMgmtIfEnableHALocal
F16683 | fsmStFailMgmtBackupBackup:backupLocal | [FSM:STAGE:FAILED¦RETRY]: internal database backup(FSM-STAGE:sam:dme:MgmtBackupBackup:backupLocal) | warning | backup-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Backup | sys/backup-[hostname] | 16683 | fsmStFailMgmtBackupBackupBackupLocal
F16683 | fsmStFailMgmtBackupBackup:upload | [FSM:STAGE:FAILED¦RETRY]: internal system backup(FSM-STAGE:sam:dme:MgmtBackupBackup:upload) | warning | upload-failed | None set. | None set. | none | TRUE | fsm | mgmt:Backup | sys/backup-[hostname] | 16683 | fsmStFailMgmtBackupBackupUpload
F16684 | fsmStFailMgmtImporterImport:config | [FSM:STAGE:FAILED¦RETRY]: importing the configuration file(FSM-STAGE:sam:dme:MgmtImporterImport:config) | warning | config-failed | None set. | None set. | none | TRUE | fsm | mgmt:Importer | sys/import-config-[hostname] | 16684 | fsmStFailMgmtImporterImportConfig
F16684 | fsmStFailMgmtImporterImport:downloadLocal | [FSM:STAGE:FAILED¦RETRY]: downloading the configuration file from the remote location(FSM-STAGE:sam:dme:MgmtImporterImport:downloadLocal) | warning | download-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Importer | sys/import-config-[hostname] | 16684 | fsmStFailMgmtImporterImportDownloadLocal
F16684 | fsmStFailMgmtImporterImport:reportResults | [FSM:STAGE:FAILED¦RETRY]: Report results of configuration application(FSM-STAGE:sam:dme:MgmtImporterImport:reportResults) | warning | report-results-failed | None set. | None set. | none | TRUE | fsm | mgmt:Importer | sys/import-config-[hostname] | 16684 | fsmStFailMgmtImporterImportReportResults
F16745 | fsmStFailQosclassDefinitionConfigGlobalQoS:SetLocal | [FSM:STAGE:FAILED¦RETRY]: QoS Classification Definition [name] configuration on primary(FSM-STAGE:sam:dme:QosclassDefinitionConfigGlobalQoS:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | qosclass:Definition | fabric/lan/classes | 16745 | fsmStFailQosclassDefinitionConfigGlobalQoSSetLocal
F16745 | fsmStFailQosclassDefinitionConfigGlobalQoS:SetPeer | [FSM:STAGE:FAILED¦RETRY]: QoS Classification Definition [name] configuration on secondary(FSM-STAGE:sam:dme:QosclassDefinitionConfigGlobalQoS:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | qosclass:Definition | fabric/lan/classes | 16745 | fsmStFailQosclassDefinitionConfigGlobalQoSSetPeer
F16750 | fsmStFailEpqosDefinitionDelTaskRemove:Local | [FSM:STAGE:FAILED¦RETRY]: vnic qos policy [name] removal from primary(FSM-STAGE:sam:dme:EpqosDefinitionDelTaskRemove:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | epqos:DefinitionDelTask | org-[name]/ep-qos-deletion-[defIntId] | 16750 | fsmStFailEpqosDefinitionDelTaskRemoveLocal
F16750 | fsmStFailEpqosDefinitionDelTaskRemove:Peer | [FSM:STAGE:FAILED¦RETRY]: vnic qos policy [name] removal from secondary(FSM-STAGE:sam:dme:EpqosDefinitionDelTaskRemove:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | epqos:DefinitionDelTask | org-[name]/ep-qos-deletion-[defIntId] | 16750 | fsmStFailEpqosDefinitionDelTaskRemovePeer
F16803 | fsmStFailEquipmentIOCardResetCmc:Execute | [FSM:STAGE:FAILED¦RETRY]: Resetting Chassis Management Controller on IOM [chassisId]/[id](FSM-STAGE:sam:dme:EquipmentIOCardResetCmc:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 16803 | fsmStFailEquipmentIOCardResetCmcExecute
F16815 | fsmStFailMgmtControllerUpdateUCSManager:execute | [FSM:STAGE:FAILED¦RETRY]: Updating UCS Manager firmware(FSM-STAGE:sam:dme:MgmtControllerUpdateUCSManager:execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16815 | fsmStFailMgmtControllerUpdateUCSManagerExecute
F16815 | fsmStFailMgmtControllerUpdateUCSManager:start | [FSM:STAGE:FAILED¦RETRY]: Scheduling UCS manager update(FSM-STAGE:sam:dme:MgmtControllerUpdateUCSManager:start) | warning | start-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16815 | fsmStFailMgmtControllerUpdateUCSManagerStart
F16823 | fsmStFailMgmtControllerSysConfig:Primary | [FSM:STAGE:FAILED¦RETRY]: system configuration on primary(FSM-STAGE:sam:dme:MgmtControllerSysConfig:Primary) | warning | primary-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16823 | fsmStFailMgmtControllerSysConfigPrimary
F16823 | fsmStFailMgmtControllerSysConfig:Secondary | [FSM:STAGE:FAILED¦RETRY]: system configuration on secondary(FSM-STAGE:sam:dme:MgmtControllerSysConfig:Secondary) | warning | secondary-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 16823 | fsmStFailMgmtControllerSysConfigSecondary
F16852 | fsmStFailAdaptorExtEthIfPathReset:Disable | [FSM:STAGE:FAILED¦RETRY]: Disable path [side]([switchId]) on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorExtEthIfPathReset:Disable) | warning | disable-failed | None set. | None set. | none | TRUE | fsm | adaptor:ExtEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/ext-eth-[id] | 16852 | fsmStFailAdaptorExtEthIfPathResetDisable
F16852 | fsmStFailAdaptorExtEthIfPathReset:Enable | [FSM:STAGE:FAILED¦RETRY]: Enabe path [side]([switchId]) on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorExtEthIfPathReset:Enable) | warning | enable-failed | None set. | None set. | none | TRUE | fsm | adaptor:ExtEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/ext-eth-[id] | 16852 | fsmStFailAdaptorExtEthIfPathResetEnable
F16857 | fsmStFailAdaptorHostEthIfCircuitReset:DisableA | [FSM:STAGE:FAILED¦RETRY]: Disable circuit A for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostEthIfCircuitReset:DisableA) | warning | disable-afailed | None set. | None set. | none | TRUE | fsm | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 16857 | fsmStFailAdaptorHostEthIfCircuitResetDisableA
F16857 | fsmStFailAdaptorHostEthIfCircuitReset:DisableB | [FSM:STAGE:FAILED¦RETRY]: Disable circuit B for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostEthIfCircuitReset:DisableB) | warning | disable-bfailed | None set. | None set. | none | TRUE | fsm | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 16857 | fsmStFailAdaptorHostEthIfCircuitResetDisableB
F16857 | fsmStFailAdaptorHostEthIfCircuitReset:EnableA | [FSM:STAGE:FAILED¦RETRY]: Enable circuit A for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostEthIfCircuitReset:EnableA) | warning | enable-afailed | None set. | None set. | none | TRUE | fsm | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 16857 | fsmStFailAdaptorHostEthIfCircuitResetEnableA
F16857 | fsmStFailAdaptorHostEthIfCircuitReset:EnableB | [FSM:STAGE:FAILED¦RETRY]: Enable circuit B for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostEthIfCircuitReset:EnableB) | warning | enable-bfailed | None set. | None set. | none | TRUE | fsm | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 16857 | fsmStFailAdaptorHostEthIfCircuitResetEnableB
F16857 | fsmStFailAdaptorHostFcIfCircuitReset:DisableA | [FSM:STAGE:FAILED¦RETRY]: Disable circuit A for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostFcIfCircuitReset:DisableA) | warning | disable-afailed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 16857 | fsmStFailAdaptorHostFcIfCircuitResetDisableA
F16857 | fsmStFailAdaptorHostFcIfCircuitReset:DisableB | [FSM:STAGE:FAILED¦RETRY]: Disable circuit B for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostFcIfCircuitReset:DisableB) | warning | disable-bfailed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 16857 | fsmStFailAdaptorHostFcIfCircuitResetDisableB
F16857 | fsmStFailAdaptorHostFcIfCircuitReset:EnableA | [FSM:STAGE:FAILED¦RETRY]: Enable circuit A for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostFcIfCircuitReset:EnableA) | warning | enable-afailed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 16857 | fsmStFailAdaptorHostFcIfCircuitResetEnableA
F16857 | fsmStFailAdaptorHostFcIfCircuitReset:EnableB | [FSM:STAGE:FAILED¦RETRY]: Enable circuit B for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostFcIfCircuitReset:EnableB) | warning | enable-bfailed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 16857 | fsmStFailAdaptorHostFcIfCircuitResetEnableB
F16879 | fsmStFailExtvmmMasterExtKeyConfig:SetLocal | [FSM:STAGE:FAILED¦RETRY]: external VM manager extension-key configuration on peer fabric(FSM-STAGE:sam:dme:ExtvmmMasterExtKeyConfig:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | extvmm:MasterExtKey | sys/extvm-mgmt/ext-key | 16879 | fsmStFailExtvmmMasterExtKeyConfigSetLocal
F16879 | fsmStFailExtvmmMasterExtKeyConfig:SetPeer | [FSM:STAGE:FAILED¦RETRY]: external VM manager extension-key configuration on local fabric(FSM-STAGE:sam:dme:ExtvmmMasterExtKeyConfig:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | extvmm:MasterExtKey | sys/extvm-mgmt/ext-key | 16879 | fsmStFailExtvmmMasterExtKeyConfigSetPeer
F16879 | fsmStFailExtvmmProviderConfig:GetVersion | [FSM:STAGE:FAILED¦RETRY]: external VM manager version fetch(FSM-STAGE:sam:dme:ExtvmmProviderConfig:GetVersion) | warning | get-version-failed | None set. | None set. | none | TRUE | fsm | extvmm:Provider | sys/extvm-mgmt/vm-[name] | 16879 | fsmStFailExtvmmProviderConfigGetVersion
F16879 | fsmStFailExtvmmProviderConfig:SetLocal | [FSM:STAGE:FAILED¦RETRY]: external VM manager configuration on local fabric(FSM-STAGE:sam:dme:ExtvmmProviderConfig:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | extvmm:Provider | sys/extvm-mgmt/vm-[name] | 16879 | fsmStFailExtvmmProviderConfigSetLocal
F16879 | fsmStFailExtvmmProviderConfig:SetPeer | [FSM:STAGE:FAILED¦RETRY]: external VM manager configuration on peer fabric(FSM-STAGE:sam:dme:ExtvmmProviderConfig:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | extvmm:Provider | sys/extvm-mgmt/vm-[name] | 16879 | fsmStFailExtvmmProviderConfigSetPeer
F16879 | fsmStFailVmLifeCyclePolicyConfig:Local | [FSM:STAGE:FAILED¦RETRY]: set Veth Auto-delete Retention Timer on local fabric(FSM-STAGE:sam:dme:VmLifeCyclePolicyConfig:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | vm:LifeCyclePolicy | org-[name]/vm-lc-policy | 16879 | fsmStFailVmLifeCyclePolicyConfigLocal
F16879 | fsmStFailVmLifeCyclePolicyConfig:Peer | [FSM:STAGE:FAILED¦RETRY]: set Veth Auto-delete Retention Timer on peer fabric(FSM-STAGE:sam:dme:VmLifeCyclePolicyConfig:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | vm:LifeCyclePolicy | org-[name]/vm-lc-policy | 16879 | fsmStFailVmLifeCyclePolicyConfigPeer
F16880 | fsmStFailExtvmmKeyStoreCertInstall:SetLocal | [FSM:STAGE:FAILED¦RETRY]: external VM manager cetificate configuration on local fabric(FSM-STAGE:sam:dme:ExtvmmKeyStoreCertInstall:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | extvmm:KeyStore | sys/extvm-mgmt/key-store | 16880 | fsmStFailExtvmmKeyStoreCertInstallSetLocal
F16880 | fsmStFailExtvmmKeyStoreCertInstall:SetPeer | [FSM:STAGE:FAILED¦RETRY]: external VM manager certificate configuration on peer fabric(FSM-STAGE:sam:dme:ExtvmmKeyStoreCertInstall:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | extvmm:KeyStore | sys/extvm-mgmt/key-store | 16880 | fsmStFailExtvmmKeyStoreCertInstallSetPeer
F16881 | fsmStFailExtvmmSwitchDelTaskRemoveProvider:RemoveLocal | [FSM:STAGE:FAILED¦RETRY]: external VM manager deletion from local fabric(FSM-STAGE:sam:dme:ExtvmmSwitchDelTaskRemoveProvider:RemoveLocal) | warning | remove-local-failed | None set. | None set. | none | TRUE | fsm | extvmm:SwitchDelTask | sys/extvm-mgmt/vsw-deltask-[swIntId] | 16881 | fsmStFailExtvmmSwitchDelTaskRemoveProviderRemoveLocal
F16904 | fsmStFailCapabilityUpdaterUpdater:Apply | [FSM:STAGE:FAILED¦RETRY]: applying changes to catalog(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:Apply) | warning | apply-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 16904 | fsmStFailCapabilityUpdaterUpdaterApply
F16904 | fsmStFailCapabilityUpdaterUpdater:CopyRemote | [FSM:STAGE:FAILED¦RETRY]: syncing catalog files to subordinate(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:CopyRemote) | warning | copy-remote-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 16904 | fsmStFailCapabilityUpdaterUpdaterCopyRemote
F16904 | fsmStFailCapabilityUpdaterUpdater:DeleteLocal | [FSM:STAGE:FAILED¦RETRY]: deleting temp image [fileName] on local(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:DeleteLocal) | warning | delete-local-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 16904 | fsmStFailCapabilityUpdaterUpdaterDeleteLocal
F16904 | fsmStFailCapabilityUpdaterUpdater:EvaluateStatus | [FSM:STAGE:FAILED¦RETRY]: evaluating status of update(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:EvaluateStatus) | warning | evaluate-status-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 16904 | fsmStFailCapabilityUpdaterUpdaterEvaluateStatus
F16904 | fsmStFailCapabilityUpdaterUpdater:Local | [FSM:STAGE:FAILED¦RETRY]: downloading catalog file [fileName] from [server](FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 16904 | fsmStFailCapabilityUpdaterUpdaterLocal
F16904 | fsmStFailCapabilityUpdaterUpdater:RescanImages | [FSM:STAGE:FAILED¦RETRY]: rescanning image files(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:RescanImages) | warning | rescan-images-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 16904 | fsmStFailCapabilityUpdaterUpdaterRescanImages
F16904 | fsmStFailCapabilityUpdaterUpdater:UnpackLocal | [FSM:STAGE:FAILED¦RETRY]: unpacking catalog file [fileName] on primary(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:UnpackLocal) | warning | unpack-local-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 16904 | fsmStFailCapabilityUpdaterUpdaterUnpackLocal
F16930 | fsmStFailComputeBladeUpdateBoardController:BladePowerOff | [FSM:STAGE:FAILED¦RETRY]: Power off server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeUpdateBoardController:BladePowerOff) | warning | blade-power-off-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16930 | fsmStFailComputeBladeUpdateBoardControllerBladePowerOff
F16930 | fsmStFailComputeBladeUpdateBoardController:BladePowerOn | [FSM:STAGE:FAILED¦RETRY]: Power on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeUpdateBoardController:BladePowerOn) | warning | blade-power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16930 | fsmStFailComputeBladeUpdateBoardControllerBladePowerOn
F16930 | fsmStFailComputeBladeUpdateBoardController:PollUpdateStatus | [FSM:STAGE:FAILED¦RETRY]: Waiting for Board Controller update to complete(FSM-STAGE:sam:dme:ComputeBladeUpdateBoardController:PollUpdateStatus) | warning | poll-update-status-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16930 | fsmStFailComputeBladeUpdateBoardControllerPollUpdateStatus
F16930 | fsmStFailComputeBladeUpdateBoardController:PrepareForUpdate | [FSM:STAGE:FAILED¦RETRY]: Prepare for BoardController update(FSM-STAGE:sam:dme:ComputeBladeUpdateBoardController:PrepareForUpdate) | warning | prepare-for-update-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16930 | fsmStFailComputeBladeUpdateBoardControllerPrepareForUpdate
F16930 | fsmStFailComputeBladeUpdateBoardController:UpdateRequest | [FSM:STAGE:FAILED¦RETRY]: Sending Board Controller update request to CIMC(FSM-STAGE:sam:dme:ComputeBladeUpdateBoardController:UpdateRequest) | warning | update-request-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 16930 | fsmStFailComputeBladeUpdateBoardControllerUpdateRequest
F16931 | fsmStFailCapabilityCatalogueDeployCatalogue:SyncBladeAGLocal | [FSM:STAGE:FAILED¦RETRY]: Sending capability catalogue [version] to local bladeAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncBladeAGLocal) | warning | sync-bladeaglocal-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 16931 | fsmStFailCapabilityCatalogueDeployCatalogueSyncBladeAGLocal
F16931 | fsmStFailCapabilityCatalogueDeployCatalogue:SyncBladeAGRemote | [FSM:STAGE:FAILED¦RETRY]: Sending capability catalogue [version] to remote bladeAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncBladeAGRemote) | warning | sync-bladeagremote-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 16931 | fsmStFailCapabilityCatalogueDeployCatalogueSyncBladeAGRemote
F16931 | fsmStFailCapabilityCatalogueDeployCatalogue:SyncHostagentAGLocal | [FSM:STAGE:FAILED¦RETRY]: Sending capability catalogue [version] to local hostagentAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncHostagentAGLocal) | warning | sync-hostagentaglocal-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 16931 | fsmStFailCapabilityCatalogueDeployCatalogueSyncHostagentAGLocal
F16931 | fsmStFailCapabilityCatalogueDeployCatalogue:SyncHostagentAGRemote | [FSM:STAGE:FAILED¦RETRY]: Sending capability catalogue [version] to remote hostagentAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncHostagentAGRemote) | warning | sync-hostagentagremote-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 16931 | fsmStFailCapabilityCatalogueDeployCatalogueSyncHostagentAGRemote
F16931 | fsmStFailCapabilityCatalogueDeployCatalogue:SyncNicAGLocal | [FSM:STAGE:FAILED¦RETRY]: Sending capability catalogue [version] to local nicAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncNicAGLocal) | warning | sync-nicaglocal-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 16931 | fsmStFailCapabilityCatalogueDeployCatalogueSyncNicAGLocal
F16931 | fsmStFailCapabilityCatalogueDeployCatalogue:SyncNicAGRemote | [FSM:STAGE:FAILED¦RETRY]: Sending capability catalogue [version] to remote nicAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncNicAGRemote) | warning | sync-nicagremote-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 16931 | fsmStFailCapabilityCatalogueDeployCatalogueSyncNicAGRemote
F16931 | fsmStFailCapabilityCatalogueDeployCatalogue:SyncPortAGLocal | [FSM:STAGE:FAILED¦RETRY]: Sending capability catalogue [version] to local portAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncPortAGLocal) | warning | sync-portaglocal-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 16931 | fsmStFailCapabilityCatalogueDeployCatalogueSyncPortAGLocal
F16931 | fsmStFailCapabilityCatalogueDeployCatalogue:SyncPortAGRemote | [FSM:STAGE:FAILED¦RETRY]: Sending capability catalogue [version] to remote portAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncPortAGRemote) | warning | sync-portagremote-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 16931 | fsmStFailCapabilityCatalogueDeployCatalogueSyncPortAGRemote
F16931 | fsmStFailCapabilityCatalogueDeployCatalogue:finalize | [FSM:STAGE:FAILED¦RETRY]: Finalizing capability catalogue [version] deployment(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:finalize) | warning | finalize-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 16931 | fsmStFailCapabilityCatalogueDeployCatalogueFinalize
F16942 | fsmStFailEquipmentFexRemoveFex:CleanupEntries | [FSM:STAGE:FAILED¦RETRY]: cleaning host entries(FSM-STAGE:sam:dme:EquipmentFexRemoveFex:CleanupEntries) | warning | cleanup-entries-failed | None set. | None set. | none | TRUE | fsm | equipment:Fex | sys/fex-[id] | 16942 | fsmStFailEquipmentFexRemoveFexCleanupEntries
F16942 | fsmStFailEquipmentFexRemoveFex:UnIdentifyLocal | [FSM:STAGE:FAILED¦RETRY]: erasing fex identity [id] from primary(FSM-STAGE:sam:dme:EquipmentFexRemoveFex:UnIdentifyLocal) | warning | un-identify-local-failed | None set. | None set. | none | TRUE | fsm | equipment:Fex | sys/fex-[id] | 16942 | fsmStFailEquipmentFexRemoveFexUnIdentifyLocal
F16942 | fsmStFailEquipmentFexRemoveFex:Wait | [FSM:STAGE:FAILED¦RETRY]: waiting for clean up of resources for chassis [id] (approx. 2 min)(FSM-STAGE:sam:dme:EquipmentFexRemoveFex:Wait) | warning | wait-failed | None set. | None set. | none | TRUE | fsm | equipment:Fex | sys/fex-[id] | 16942 | fsmStFailEquipmentFexRemoveFexWait
F16942 | fsmStFailEquipmentFexRemoveFex:decomission | [FSM:STAGE:FAILED¦RETRY]: decomissioning fex [id](FSM-STAGE:sam:dme:EquipmentFexRemoveFex:decomission) | warning | decomission-failed | None set. | None set. | none | TRUE | fsm | equipment:Fex | sys/fex-[id] | 16942 | fsmStFailEquipmentFexRemoveFexDecomission
F16943 | fsmStFailEquipmentLocatorLedSetFeLocatorLed:Execute | [FSM:STAGE:FAILED¦RETRY]: setting locator led to [adminState](FSM-STAGE:sam:dme:EquipmentLocatorLedSetFeLocatorLed:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:LocatorLed | sys/chassis-[id]/blade-[slotId]/locator-led | 16943 | fsmStFailEquipmentLocatorLedSetFeLocatorLedExecute
F16944 | fsmStFailComputePhysicalPowerCap:Config | [FSM:STAGE:FAILED¦RETRY]: Configuring power cap of server [dn](FSM-STAGE:sam:dme:ComputePhysicalPowerCap:Config) | warning | config-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16944 | fsmStFailComputePhysicalPowerCapConfig
F16944 | fsmStFailEquipmentChassisPowerCap:Config | [FSM:STAGE:FAILED¦RETRY]: (FSM-STAGE:sam:dme:EquipmentChassisPowerCap:Config) | warning | config-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 16944 | fsmStFailEquipmentChassisPowerCapConfig
F16945 | fsmStFailEquipmentIOCardMuxOffline:CleanupEntries | [FSM:STAGE:FAILED¦RETRY]: cleaning host entries(FSM-STAGE:sam:dme:EquipmentIOCardMuxOffline:CleanupEntries) | warning | cleanup-entries-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 16945 | fsmStFailEquipmentIOCardMuxOfflineCleanupEntries
F16973 | fsmStFailComputePhysicalAssociate:ActivateBios | [FSM:STAGE:FAILED¦RETRY]: Activate BIOS image for server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:ActivateBios) | warning | activate-bios-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateActivateBios
F16973 | fsmStFailComputePhysicalAssociate:BiosImgUpdate | [FSM:STAGE:FAILED¦RETRY]: Update blade BIOS image(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BiosImgUpdate) | warning | bios-img-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateBiosImgUpdate
F16973 | fsmStFailComputePhysicalAssociate:BiosPostCompletion | [FSM:STAGE:FAILED¦RETRY]: Waiting for BIOS POST completion from CIMC on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:BiosPostCompletion) | warning | bios-post-completion-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateBiosPostCompletion
F16973 | fsmStFailComputePhysicalAssociate:BladePowerOff | [FSM:STAGE:FAILED¦RETRY]: Power off server for configuration of service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:BladePowerOff) | warning | blade-power-off-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateBladePowerOff
F16973 | fsmStFailComputePhysicalAssociate:BmcConfigPnuOS | [FSM:STAGE:FAILED¦RETRY]: provisioning a bootable device with a bootable pre-boot image for server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BmcConfigPnuOS) | warning | bmc-config-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateBmcConfigPnuOS
F16973 | fsmStFailComputePhysicalAssociate:BmcPreconfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BmcPreconfigPnuOSLocal) | warning | bmc-preconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateBmcPreconfigPnuOSLocal
F16973 | fsmStFailComputePhysicalAssociate:BmcPreconfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BmcPreconfigPnuOSPeer) | warning | bmc-preconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateBmcPreconfigPnuOSPeer
F16973 | fsmStFailComputePhysicalAssociate:BmcUnconfigPnuOS | [FSM:STAGE:FAILED¦RETRY]: unprovisioning the bootable device for server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BmcUnconfigPnuOS) | warning | bmc-unconfig-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateBmcUnconfigPnuOS
F16973 | fsmStFailComputePhysicalAssociate:BootHost | [FSM:STAGE:FAILED¦RETRY]: Boot host OS for server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BootHost) | warning | boot-host-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateBootHost
F16973 | fsmStFailComputePhysicalAssociate:BootPnuos | [FSM:STAGE:FAILED¦RETRY]: Bring-up pre-boot environment for association with [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:BootPnuos) | warning | boot-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateBootPnuos
F16973 | fsmStFailComputePhysicalAssociate:BootWait | [FSM:STAGE:FAILED¦RETRY]: Waiting for system reset(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BootWait) | warning | boot-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateBootWait
F16973 | fsmStFailComputePhysicalAssociate:ClearBiosUpdate | [FSM:STAGE:FAILED¦RETRY]: Clearing pending BIOS image update(FSM-STAGE:sam:dme:ComputePhysicalAssociate:ClearBiosUpdate) | warning | clear-bios-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateClearBiosUpdate
F16973 | fsmStFailComputePhysicalAssociate:ConfigSoL | [FSM:STAGE:FAILED¦RETRY]: Configuring SoL interface on server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:ConfigSoL) | warning | config-so-lfailed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateConfigSoL
F16973 | fsmStFailComputePhysicalAssociate:ConfigUserAccess | [FSM:STAGE:FAILED¦RETRY]: Configuring external user access(FSM-STAGE:sam:dme:ComputePhysicalAssociate:ConfigUserAccess) | warning | config-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateConfigUserAccess
F16973 | fsmStFailComputePhysicalAssociate:ConfigUuid | [FSM:STAGE:FAILED¦RETRY]: Configure logical UUID for server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:ConfigUuid) | warning | config-uuid-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateConfigUuid
F16973 | fsmStFailComputePhysicalAssociate:HbaImgUpdate | [FSM:STAGE:FAILED¦RETRY]: Update Host Bus Adapter image(FSM-STAGE:sam:dme:ComputePhysicalAssociate:HbaImgUpdate) | warning | hba-img-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateHbaImgUpdate
F16973 | fsmStFailComputePhysicalAssociate:HostOSConfig | [FSM:STAGE:FAILED¦RETRY]: Configure host OS components on server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:HostOSConfig) | warning | hostosconfig-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateHostOSConfig
F16973 | fsmStFailComputePhysicalAssociate:HostOSIdent | [FSM:STAGE:FAILED¦RETRY]: Identify host agent on server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:HostOSIdent) | warning | hostosident-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateHostOSIdent
F16973 | fsmStFailComputePhysicalAssociate:HostOSPolicy | [FSM:STAGE:FAILED¦RETRY]: Upload host agent policy to host agent on server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:HostOSPolicy) | warning | hostospolicy-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateHostOSPolicy
F16973 | fsmStFailComputePhysicalAssociate:HostOSValidate | [FSM:STAGE:FAILED¦RETRY]: Validate host OS on server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:HostOSValidate) | warning | hostosvalidate-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateHostOSValidate
F16973 | fsmStFailComputePhysicalAssociate:LocalDiskFwUpdate | [FSM:STAGE:FAILED¦RETRY]: Update LocalDisk firmware image(FSM-STAGE:sam:dme:ComputePhysicalAssociate:LocalDiskFwUpdate) | warning | local-disk-fw-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateLocalDiskFwUpdate
F16973 | fsmStFailComputePhysicalAssociate:NicConfigHostOSLocal | [FSM:STAGE:FAILED¦RETRY]: Configure adapter in server for host OS (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicConfigHostOSLocal) | warning | nic-config-hostoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateNicConfigHostOSLocal
F16973 | fsmStFailComputePhysicalAssociate:NicConfigHostOSPeer | [FSM:STAGE:FAILED¦RETRY]: Configure adapter in server for host OS (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicConfigHostOSPeer) | warning | nic-config-hostospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateNicConfigHostOSPeer
F16973 | fsmStFailComputePhysicalAssociate:NicConfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: Configure adapter for pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicConfigPnuOSLocal) | warning | nic-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateNicConfigPnuOSLocal
F16973 | fsmStFailComputePhysicalAssociate:NicConfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: Configure adapter for pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicConfigPnuOSPeer) | warning | nic-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateNicConfigPnuOSPeer
F16973 | fsmStFailComputePhysicalAssociate:NicImgUpdate | [FSM:STAGE:FAILED¦RETRY]: Update adapter image(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicImgUpdate) | warning | nic-img-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateNicImgUpdate
F16973 | fsmStFailComputePhysicalAssociate:NicUnconfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfigure adapter of server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicUnconfigPnuOSLocal) | warning | nic-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateNicUnconfigPnuOSLocal
F16973 | fsmStFailComputePhysicalAssociate:NicUnconfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfigure adapter of server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicUnconfigPnuOSPeer) | warning | nic-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateNicUnconfigPnuOSPeer
F16973 | fsmStFailComputePhysicalAssociate:PnuOSCatalog | [FSM:STAGE:FAILED¦RETRY]: Populate pre-boot catalog to server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSCatalog) | warning | pnuoscatalog-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePnuOSCatalog
F16973 | fsmStFailComputePhysicalAssociate:PnuOSConfig | [FSM:STAGE:FAILED¦RETRY]: Configure server with service profile [assignedToDn] pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSConfig) | warning | pnuosconfig-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePnuOSConfig
F16973 | fsmStFailComputePhysicalAssociate:PnuOSIdent | [FSM:STAGE:FAILED¦RETRY]: Identify pre-boot environment agent(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSIdent) | warning | pnuosident-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePnuOSIdent
F16973 | fsmStFailComputePhysicalAssociate:PnuOSInventory | [FSM:STAGE:FAILED¦RETRY]: Perform inventory of server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSInventory) | warning | pnuosinventory-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePnuOSInventory
F16973 | fsmStFailComputePhysicalAssociate:PnuOSLocalDiskConfig | [FSM:STAGE:FAILED¦RETRY]: Configure local disk on server with service profile [assignedToDn] pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSLocalDiskConfig) | warning | pnuoslocal-disk-config-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePnuOSLocalDiskConfig
F16973 | fsmStFailComputePhysicalAssociate:PnuOSPolicy | [FSM:STAGE:FAILED¦RETRY]: Populate pre-boot environment behavior policy(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSPolicy) | warning | pnuospolicy-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePnuOSPolicy
F16973 | fsmStFailComputePhysicalAssociate:PnuOSSelfTest | [FSM:STAGE:FAILED¦RETRY]: Trigger self-test on pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSSelfTest) | warning | pnuosself-test-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePnuOSSelfTest
F16973 | fsmStFailComputePhysicalAssociate:PnuOSUnloadDrivers | [FSM:STAGE:FAILED¦RETRY]: Unload drivers on server with service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSUnloadDrivers) | warning | pnuosunload-drivers-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePnuOSUnloadDrivers
F16973 | fsmStFailComputePhysicalAssociate:PnuOSValidate | [FSM:STAGE:FAILED¦RETRY]: Pre-boot environment validation for association with [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSValidate) | warning | pnuosvalidate-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePnuOSValidate
F16973 | fsmStFailComputePhysicalAssociate:PollBiosActivateStatus | [FSM:STAGE:FAILED¦RETRY]: waiting for BIOS activate(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PollBiosActivateStatus) | warning | poll-bios-activate-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePollBiosActivateStatus
F16973 | fsmStFailComputePhysicalAssociate:PollBiosUpdateStatus | [FSM:STAGE:FAILED¦RETRY]: Waiting for BIOS update to complete(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PollBiosUpdateStatus) | warning | poll-bios-update-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePollBiosUpdateStatus
F16973 | fsmStFailComputePhysicalAssociate:PollBoardCtrlUpdateStatus | [FSM:STAGE:FAILED¦RETRY]: Waiting for Board Controller update to complete(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PollBoardCtrlUpdateStatus) | warning | poll-board-ctrl-update-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePollBoardCtrlUpdateStatus
F16973 | fsmStFailComputePhysicalAssociate:PollClearBiosUpdateStatus | [FSM:STAGE:FAILED¦RETRY]: waiting for pending BIOS image update to clear(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PollClearBiosUpdateStatus) | warning | poll-clear-bios-update-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePollClearBiosUpdateStatus
F16973 | fsmStFailComputePhysicalAssociate:PowerOn | [FSM:STAGE:FAILED¦RETRY]: Power on server for configuration of service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:PowerOn) | warning | power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePowerOn
F16973 | fsmStFailComputePhysicalAssociate:PreSanitize | [FSM:STAGE:FAILED¦RETRY]: Preparing to check hardware configuration(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePreSanitize
F16973 | fsmStFailComputePhysicalAssociate:PrepareForBoot | [FSM:STAGE:FAILED¦RETRY]: Prepare server for booting host OS(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PrepareForBoot) | warning | prepare-for-boot-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociatePrepareForBoot
F16973 | fsmStFailComputePhysicalAssociate:Sanitize | [FSM:STAGE:FAILED¦RETRY]: Checking hardware configuration(FSM-STAGE:sam:dme:ComputePhysicalAssociate:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSanitize
F16973 | fsmStFailComputePhysicalAssociate:SolRedirectDisable | [FSM:STAGE:FAILED¦RETRY]: Disable Sol Redirection on server [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:SolRedirectDisable) | warning | sol-redirect-disable-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSolRedirectDisable
F16973 | fsmStFailComputePhysicalAssociate:SolRedirectEnable | [FSM:STAGE:FAILED¦RETRY]: set up bios token for server [assignedToDn] for Sol redirect(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SolRedirectEnable) | warning | sol-redirect-enable-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSolRedirectEnable
F16973 | fsmStFailComputePhysicalAssociate:StorageCtlrImgUpdate | [FSM:STAGE:FAILED¦RETRY]: Update storage controller image(FSM-STAGE:sam:dme:ComputePhysicalAssociate:StorageCtlrImgUpdate) | warning | storage-ctlr-img-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateStorageCtlrImgUpdate
F16973 | fsmStFailComputePhysicalAssociate:SwConfigHostOSLocal | [FSM:STAGE:FAILED¦RETRY]: Configure primary fabric interconnect for server host os (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigHostOSLocal) | warning | sw-config-hostoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSwConfigHostOSLocal
F16973 | fsmStFailComputePhysicalAssociate:SwConfigHostOSPeer | [FSM:STAGE:FAILED¦RETRY]: Configure secondary fabric interconnect for server host OS (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigHostOSPeer) | warning | sw-config-hostospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSwConfigHostOSPeer
F16973 | fsmStFailComputePhysicalAssociate:SwConfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: Configure primary fabric interconnect for pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigPnuOSLocal) | warning | sw-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSwConfigPnuOSLocal
F16973 | fsmStFailComputePhysicalAssociate:SwConfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: Configure secondary fabric interconnect for pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigPnuOSPeer) | warning | sw-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSwConfigPnuOSPeer
F16973 | fsmStFailComputePhysicalAssociate:SwConfigPortNivLocal | [FSM:STAGE:FAILED¦RETRY]: configuring primary fabric interconnect access to server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigPortNivLocal) | warning | sw-config-port-niv-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSwConfigPortNivLocal
F16973 | fsmStFailComputePhysicalAssociate:SwConfigPortNivPeer | [FSM:STAGE:FAILED¦RETRY]: configuring secondary fabric interconnect access to server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigPortNivPeer) | warning | sw-config-port-niv-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSwConfigPortNivPeer
F16973 | fsmStFailComputePhysicalAssociate:SwUnconfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfigure primary fabric interconnect for server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwUnconfigPnuOSLocal) | warning | sw-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSwUnconfigPnuOSLocal
F16973 | fsmStFailComputePhysicalAssociate:SwUnconfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfigure secondary fabric interconnect for server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwUnconfigPnuOSPeer) | warning | sw-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSwUnconfigPnuOSPeer
F16973 | fsmStFailComputePhysicalAssociate:UpdateBiosRequest | [FSM:STAGE:FAILED¦RETRY]: Sending update BIOS request to CIMC(FSM-STAGE:sam:dme:ComputePhysicalAssociate:UpdateBiosRequest) | warning | update-bios-request-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateUpdateBiosRequest
F16973 | fsmStFailComputePhysicalAssociate:UpdateBoardCtrlRequest | [FSM:STAGE:FAILED¦RETRY]: Sending Board Controller update request to CIMC(FSM-STAGE:sam:dme:ComputePhysicalAssociate:UpdateBoardCtrlRequest) | warning | update-board-ctrl-request-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateUpdateBoardCtrlRequest
F16973 | fsmStFailComputePhysicalAssociate:activateAdaptorNwFwLocal | [FSM:STAGE:FAILED¦RETRY]: Activate adapter network firmware on(FSM-STAGE:sam:dme:ComputePhysicalAssociate:activateAdaptorNwFwLocal) | warning | activate-adaptor-nw-fw-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateActivateAdaptorNwFwLocal
F16973 | fsmStFailComputePhysicalAssociate:activateAdaptorNwFwPeer | [FSM:STAGE:FAILED¦RETRY]: Activate adapter network firmware on(FSM-STAGE:sam:dme:ComputePhysicalAssociate:activateAdaptorNwFwPeer) | warning | activate-adaptor-nw-fw-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateActivateAdaptorNwFwPeer
F16973 | fsmStFailComputePhysicalAssociate:activateIBMCFw | [FSM:STAGE:FAILED¦RETRY]: Activate CIMC firmware of server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:activateIBMCFw) | warning | activateibmcfw-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateActivateIBMCFw
F16973 | fsmStFailComputePhysicalAssociate:hagHostOSConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to host agent on server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:hagHostOSConnect) | warning | hag-hostosconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateHagHostOSConnect
F16973 | fsmStFailComputePhysicalAssociate:hagPnuOSConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to pre-boot environment agent for association with [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:hagPnuOSConnect) | warning | hag-pnuosconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateHagPnuOSConnect
F16973 | fsmStFailComputePhysicalAssociate:hagPnuOSDisconnect | [FSM:STAGE:FAILED¦RETRY]: Disconnect pre-boot environment agent(FSM-STAGE:sam:dme:ComputePhysicalAssociate:hagPnuOSDisconnect) | warning | hag-pnuosdisconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateHagPnuOSDisconnect
F16973 | fsmStFailComputePhysicalAssociate:resetIBMC | [FSM:STAGE:FAILED¦RETRY]: Reset CIMC of server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:resetIBMC) | warning | resetibmc-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateResetIBMC
F16973 | fsmStFailComputePhysicalAssociate:serialDebugPnuOSConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to pre-boot environment agent for association with [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:serialDebugPnuOSConnect) | warning | serial-debug-pnuosconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSerialDebugPnuOSConnect
F16973 | fsmStFailComputePhysicalAssociate:serialDebugPnuOSDisconnect | [FSM:STAGE:FAILED¦RETRY]: Disconnect pre-boot environment agent(FSM-STAGE:sam:dme:ComputePhysicalAssociate:serialDebugPnuOSDisconnect) | warning | serial-debug-pnuosdisconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateSerialDebugPnuOSDisconnect
F16973 | fsmStFailComputePhysicalAssociate:updateAdaptorNwFwLocal | [FSM:STAGE:FAILED¦RETRY]: Update adapter network firmware(FSM-STAGE:sam:dme:ComputePhysicalAssociate:updateAdaptorNwFwLocal) | warning | update-adaptor-nw-fw-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateUpdateAdaptorNwFwLocal
F16973 | fsmStFailComputePhysicalAssociate:updateAdaptorNwFwPeer | [FSM:STAGE:FAILED¦RETRY]: Update adapter network firmware(FSM-STAGE:sam:dme:ComputePhysicalAssociate:updateAdaptorNwFwPeer) | warning | update-adaptor-nw-fw-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateUpdateAdaptorNwFwPeer
F16973 | fsmStFailComputePhysicalAssociate:updateIBMCFw | [FSM:STAGE:FAILED¦RETRY]: Update CIMC firmware of server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:updateIBMCFw) | warning | updateibmcfw-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateUpdateIBMCFw
F16973 | fsmStFailComputePhysicalAssociate:waitForAdaptorNwFwUpdateLocal | [FSM:STAGE:FAILED¦RETRY]: Wait for adapter network firmware update completion(FSM-STAGE:sam:dme:ComputePhysicalAssociate:waitForAdaptorNwFwUpdateLocal) | warning | wait-for-adaptor-nw-fw-update-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateWaitForAdaptorNwFwUpdateLocal
F16973 | fsmStFailComputePhysicalAssociate:waitForAdaptorNwFwUpdatePeer | [FSM:STAGE:FAILED¦RETRY]: Wait for adapter network firmware update completion(FSM-STAGE:sam:dme:ComputePhysicalAssociate:waitForAdaptorNwFwUpdatePeer) | warning | wait-for-adaptor-nw-fw-update-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateWaitForAdaptorNwFwUpdatePeer
F16973 | fsmStFailComputePhysicalAssociate:waitForIBMCFwUpdate | [FSM:STAGE:FAILED¦RETRY]: Wait for CIMC firmware completion on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:waitForIBMCFwUpdate) | warning | wait-foribmcfw-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16973 | fsmStFailComputePhysicalAssociateWaitForIBMCFwUpdate
F16974 | fsmStFailComputePhysicalDisassociate:BiosPostCompletion | [FSM:STAGE:FAILED¦RETRY]: Waiting for BIOS POST completion from CIMC on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BiosPostCompletion) | warning | bios-post-completion-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateBiosPostCompletion
F16974 | fsmStFailComputePhysicalDisassociate:BmcConfigPnuOS | [FSM:STAGE:FAILED¦RETRY]: provisioning a bootable device with a bootable pre-boot image for server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BmcConfigPnuOS) | warning | bmc-config-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateBmcConfigPnuOS
F16974 | fsmStFailComputePhysicalDisassociate:BmcPreconfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BmcPreconfigPnuOSLocal) | warning | bmc-preconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateBmcPreconfigPnuOSLocal
F16974 | fsmStFailComputePhysicalDisassociate:BmcPreconfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BmcPreconfigPnuOSPeer) | warning | bmc-preconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateBmcPreconfigPnuOSPeer
F16974 | fsmStFailComputePhysicalDisassociate:BmcUnconfigPnuOS | [FSM:STAGE:FAILED¦RETRY]: unprovisioning the bootable device for server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BmcUnconfigPnuOS) | warning | bmc-unconfig-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateBmcUnconfigPnuOS
F16974 | fsmStFailComputePhysicalDisassociate:BootPnuos | [FSM:STAGE:FAILED¦RETRY]: Bring-up pre-boot environment on server for disassociation with service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BootPnuos) | warning | boot-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateBootPnuos
F16974 | fsmStFailComputePhysicalDisassociate:BootWait | [FSM:STAGE:FAILED¦RETRY]: Waiting for system reset on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BootWait) | warning | boot-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateBootWait
F16974 | fsmStFailComputePhysicalDisassociate:ConfigBios | [FSM:STAGE:FAILED¦RETRY]: Configuring BIOS Defaults on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:ConfigBios) | warning | config-bios-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateConfigBios
F16974 | fsmStFailComputePhysicalDisassociate:ConfigUserAccess | [FSM:STAGE:FAILED¦RETRY]: Configuring external user access(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:ConfigUserAccess) | warning | config-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateConfigUserAccess
F16974 | fsmStFailComputePhysicalDisassociate:HandlePooling | [FSM:STAGE:FAILED¦RETRY]: Apply post-disassociation policies to server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:HandlePooling) | warning | handle-pooling-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateHandlePooling
F16974 | fsmStFailComputePhysicalDisassociate:NicConfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: Configure adapter for pre-boot environment on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicConfigPnuOSLocal) | warning | nic-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateNicConfigPnuOSLocal
F16974 | fsmStFailComputePhysicalDisassociate:NicConfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: Configure adapter for pre-boot environment on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicConfigPnuOSPeer) | warning | nic-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateNicConfigPnuOSPeer
F16974 | fsmStFailComputePhysicalDisassociate:NicUnconfigHostOSLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfigure host OS connectivity from server adapter(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicUnconfigHostOSLocal) | warning | nic-unconfig-hostoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateNicUnconfigHostOSLocal
F16974 | fsmStFailComputePhysicalDisassociate:NicUnconfigHostOSPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfigure host OS connectivity from server adapter(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicUnconfigHostOSPeer) | warning | nic-unconfig-hostospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateNicUnconfigHostOSPeer
F16974 | fsmStFailComputePhysicalDisassociate:NicUnconfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfigure adapter of server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicUnconfigPnuOSLocal) | warning | nic-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateNicUnconfigPnuOSLocal
F16974 | fsmStFailComputePhysicalDisassociate:NicUnconfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfigure adapter of server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicUnconfigPnuOSPeer) | warning | nic-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateNicUnconfigPnuOSPeer
F16974 | fsmStFailComputePhysicalDisassociate:PnuOSCatalog | [FSM:STAGE:FAILED¦RETRY]: Populate pre-boot catalog to server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSCatalog) | warning | pnuoscatalog-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociatePnuOSCatalog
F16974 | fsmStFailComputePhysicalDisassociate:PnuOSIdent | [FSM:STAGE:FAILED¦RETRY]: Identify pre-boot environment agent on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSIdent) | warning | pnuosident-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociatePnuOSIdent
F16974 | fsmStFailComputePhysicalDisassociate:PnuOSPolicy | [FSM:STAGE:FAILED¦RETRY]: Populate pre-boot environment behavior policy to server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSPolicy) | warning | pnuospolicy-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociatePnuOSPolicy
F16974 | fsmStFailComputePhysicalDisassociate:PnuOSScrub | [FSM:STAGE:FAILED¦RETRY]: Scrub server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSScrub) | warning | pnuosscrub-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociatePnuOSScrub
F16974 | fsmStFailComputePhysicalDisassociate:PnuOSSelfTest | [FSM:STAGE:FAILED¦RETRY]: Trigger self-test of server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSSelfTest) | warning | pnuosself-test-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociatePnuOSSelfTest
F16974 | fsmStFailComputePhysicalDisassociate:PnuOSUnconfig | [FSM:STAGE:FAILED¦RETRY]: Unconfigure server from service profile [assignedToDn] pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSUnconfig) | warning | pnuosunconfig-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociatePnuOSUnconfig
F16974 | fsmStFailComputePhysicalDisassociate:PnuOSValidate | [FSM:STAGE:FAILED¦RETRY]: Pre-boot environment validate server for disassociation with service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSValidate) | warning | pnuosvalidate-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociatePnuOSValidate
F16974 | fsmStFailComputePhysicalDisassociate:PowerOn | [FSM:STAGE:FAILED¦RETRY]: Power on server for unconfiguration of service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PowerOn) | warning | power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociatePowerOn
F16974 | fsmStFailComputePhysicalDisassociate:PreSanitize | [FSM:STAGE:FAILED¦RETRY]: Preparing to check hardware configuration server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociatePreSanitize
F16974 | fsmStFailComputePhysicalDisassociate:Sanitize | [FSM:STAGE:FAILED¦RETRY]: Checking hardware configuration server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSanitize
F16974 | fsmStFailComputePhysicalDisassociate:Shutdown | [FSM:STAGE:FAILED¦RETRY]: Shutdown server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:Shutdown) | warning | shutdown-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateShutdown
F16974 | fsmStFailComputePhysicalDisassociate:SolRedirectDisable | [FSM:STAGE:FAILED¦RETRY]: Disable Sol redirection on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SolRedirectDisable) | warning | sol-redirect-disable-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSolRedirectDisable
F16974 | fsmStFailComputePhysicalDisassociate:SolRedirectEnable | [FSM:STAGE:FAILED¦RETRY]: set up bios token for server [serverId] for Sol redirect(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SolRedirectEnable) | warning | sol-redirect-enable-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSolRedirectEnable
F16974 | fsmStFailComputePhysicalDisassociate:SwConfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: Configure primary fabric interconnect for pre-boot environment on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwConfigPnuOSLocal) | warning | sw-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSwConfigPnuOSLocal
F16974 | fsmStFailComputePhysicalDisassociate:SwConfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: Configure secondary fabric interconnect for pre-boot environment on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwConfigPnuOSPeer) | warning | sw-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSwConfigPnuOSPeer
F16974 | fsmStFailComputePhysicalDisassociate:SwConfigPortNivLocal | [FSM:STAGE:FAILED¦RETRY]: configuring primary fabric interconnect access to server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwConfigPortNivLocal) | warning | sw-config-port-niv-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSwConfigPortNivLocal
F16974 | fsmStFailComputePhysicalDisassociate:SwConfigPortNivPeer | [FSM:STAGE:FAILED¦RETRY]: configuring secondary fabric interconnect access to server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwConfigPortNivPeer) | warning | sw-config-port-niv-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSwConfigPortNivPeer
F16974 | fsmStFailComputePhysicalDisassociate:SwUnconfigHostOSLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfigure host OS connectivity from server to primary fabric interconnect(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwUnconfigHostOSLocal) | warning | sw-unconfig-hostoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSwUnconfigHostOSLocal
F16974 | fsmStFailComputePhysicalDisassociate:SwUnconfigHostOSPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfigure host OS connectivity from server to secondary fabric interconnect(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwUnconfigHostOSPeer) | warning | sw-unconfig-hostospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSwUnconfigHostOSPeer
F16974 | fsmStFailComputePhysicalDisassociate:SwUnconfigPnuOSLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfigure primary fabric interconnect for server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwUnconfigPnuOSLocal) | warning | sw-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSwUnconfigPnuOSLocal
F16974 | fsmStFailComputePhysicalDisassociate:SwUnconfigPnuOSPeer | [FSM:STAGE:FAILED¦RETRY]: Unconfigure secondary fabric interconnect for server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwUnconfigPnuOSPeer) | warning | sw-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSwUnconfigPnuOSPeer
F16974 | fsmStFailComputePhysicalDisassociate:UnconfigBios | [FSM:STAGE:FAILED¦RETRY]: Unconfiguring BIOS Settings and Boot Order of server [serverId] (service profile [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:UnconfigBios) | warning | unconfig-bios-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateUnconfigBios
F16974 | fsmStFailComputePhysicalDisassociate:UnconfigSoL | [FSM:STAGE:FAILED¦RETRY]: Removing SoL configuration from server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:UnconfigSoL) | warning | unconfig-so-lfailed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateUnconfigSoL
F16974 | fsmStFailComputePhysicalDisassociate:UnconfigUuid | [FSM:STAGE:FAILED¦RETRY]: Restore original UUID for server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:UnconfigUuid) | warning | unconfig-uuid-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateUnconfigUuid
F16974 | fsmStFailComputePhysicalDisassociate:hagPnuOSConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to pre-boot environment agent on server for disassociation with service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:hagPnuOSConnect) | warning | hag-pnuosconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateHagPnuOSConnect
F16974 | fsmStFailComputePhysicalDisassociate:hagPnuOSDisconnect | [FSM:STAGE:FAILED¦RETRY]: Disconnect pre-boot environment agent for server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:hagPnuOSDisconnect) | warning | hag-pnuosdisconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateHagPnuOSDisconnect
F16974 | fsmStFailComputePhysicalDisassociate:serialDebugPnuOSConnect | [FSM:STAGE:FAILED¦RETRY]: Connect to pre-boot environment agent on server for disassociation with service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:serialDebugPnuOSConnect) | warning | serial-debug-pnuosconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSerialDebugPnuOSConnect
F16974 | fsmStFailComputePhysicalDisassociate:serialDebugPnuOSDisconnect | [FSM:STAGE:FAILED¦RETRY]: Disconnect pre-boot environment agent for server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:serialDebugPnuOSDisconnect) | warning | serial-debug-pnuosdisconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16974 | fsmStFailComputePhysicalDisassociateSerialDebugPnuOSDisconnect
F16976 | fsmStFailComputePhysicalDecommission:CleanupCIMC | [FSM:STAGE:FAILED¦RETRY]: Cleaning up CIMC configuration for server [dn](FSM-STAGE:sam:dme:ComputePhysicalDecommission:CleanupCIMC) | warning | cleanupcimc-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16976 | fsmStFailComputePhysicalDecommissionCleanupCIMC
F16976 | fsmStFailComputePhysicalDecommission:Execute | [FSM:STAGE:FAILED¦RETRY]: Decommissioning server [dn](FSM-STAGE:sam:dme:ComputePhysicalDecommission:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16976 | fsmStFailComputePhysicalDecommissionExecute
F16976 | fsmStFailComputePhysicalDecommission:StopVMediaLocal | [FSM:STAGE:FAILED¦RETRY]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalDecommission:StopVMediaLocal) | warning | stopvmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16976 | fsmStFailComputePhysicalDecommissionStopVMediaLocal
F16976 | fsmStFailComputePhysicalDecommission:StopVMediaPeer | [FSM:STAGE:FAILED¦RETRY]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalDecommission:StopVMediaPeer) | warning | stopvmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16976 | fsmStFailComputePhysicalDecommissionStopVMediaPeer
F16977 | fsmStFailComputePhysicalSoftShutdown:Execute | [FSM:STAGE:FAILED¦RETRY]: Soft shutdown of server [dn](FSM-STAGE:sam:dme:ComputePhysicalSoftShutdown:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16977 | fsmStFailComputePhysicalSoftShutdownExecute
F16978 | fsmStFailComputePhysicalHardShutdown:Execute | [FSM:STAGE:FAILED¦RETRY]: Hard shutdown of server [dn](FSM-STAGE:sam:dme:ComputePhysicalHardShutdown:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16978 | fsmStFailComputePhysicalHardShutdownExecute
F16979 | fsmStFailComputePhysicalTurnup:Execute | [FSM:STAGE:FAILED¦RETRY]: Power-on server [dn](FSM-STAGE:sam:dme:ComputePhysicalTurnup:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16979 | fsmStFailComputePhysicalTurnupExecute
F16980 | fsmStFailComputePhysicalPowercycle:Execute | [FSM:STAGE:FAILED¦RETRY]: Power-cycle server [dn](FSM-STAGE:sam:dme:ComputePhysicalPowercycle:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16980 | fsmStFailComputePhysicalPowercycleExecute
F16980 | fsmStFailComputePhysicalPowercycle:PreSanitize | [FSM:STAGE:FAILED¦RETRY]: Preparing to check hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalPowercycle:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16980 | fsmStFailComputePhysicalPowercyclePreSanitize
F16980 | fsmStFailComputePhysicalPowercycle:Sanitize | [FSM:STAGE:FAILED¦RETRY]: Checking hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalPowercycle:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16980 | fsmStFailComputePhysicalPowercycleSanitize
F16981 | fsmStFailComputePhysicalHardreset:Execute | [FSM:STAGE:FAILED¦RETRY]: Hard-reset server [dn](FSM-STAGE:sam:dme:ComputePhysicalHardreset:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16981 | fsmStFailComputePhysicalHardresetExecute
F16981 | fsmStFailComputePhysicalHardreset:PreSanitize | [FSM:STAGE:FAILED¦RETRY]: Preparing to check hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalHardreset:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16981 | fsmStFailComputePhysicalHardresetPreSanitize
F16981 | fsmStFailComputePhysicalHardreset:Sanitize | [FSM:STAGE:FAILED¦RETRY]: Checking hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalHardreset:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16981 | fsmStFailComputePhysicalHardresetSanitize
F16982 | fsmStFailComputePhysicalSoftreset:Execute | [FSM:STAGE:FAILED¦RETRY]: Soft-reset server [dn](FSM-STAGE:sam:dme:ComputePhysicalSoftreset:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16982 | fsmStFailComputePhysicalSoftresetExecute
F16982 | fsmStFailComputePhysicalSoftreset:PreSanitize | [FSM:STAGE:FAILED¦RETRY]: Preparing to check hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalSoftreset:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16982 | fsmStFailComputePhysicalSoftresetPreSanitize
F16982 | fsmStFailComputePhysicalSoftreset:Sanitize | [FSM:STAGE:FAILED¦RETRY]: Checking hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalSoftreset:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16982 | fsmStFailComputePhysicalSoftresetSanitize
F16983 | fsmStFailComputePhysicalSwConnUpd:A | [FSM:STAGE:FAILED¦RETRY]: Updating fabric A for server [dn](FSM-STAGE:sam:dme:ComputePhysicalSwConnUpd:A) | warning | a-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16983 | fsmStFailComputePhysicalSwConnUpdA
F16983 | fsmStFailComputePhysicalSwConnUpd:B | [FSM:STAGE:FAILED¦RETRY]: Updating fabric B for server [dn](FSM-STAGE:sam:dme:ComputePhysicalSwConnUpd:B) | warning | b-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16983 | fsmStFailComputePhysicalSwConnUpdB
F16984 | fsmStFailComputePhysicalBiosRecovery:Cleanup | [FSM:STAGE:FAILED¦RETRY]: Completing BIOS recovery mode for server [dn], and shutting it down(FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Cleanup) | warning | cleanup-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoveryCleanup
F16984 | fsmStFailComputePhysicalBiosRecovery:PreSanitize | [FSM:STAGE:FAILED¦RETRY]: Preparing to check hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoveryPreSanitize
F16984 | fsmStFailComputePhysicalBiosRecovery:Reset | [FSM:STAGE:FAILED¦RETRY]: Resetting server [dn] power state after BIOS recovery(FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Reset) | warning | reset-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoveryReset
F16984 | fsmStFailComputePhysicalBiosRecovery:Sanitize | [FSM:STAGE:FAILED¦RETRY]: Checking hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoverySanitize
F16984 | fsmStFailComputePhysicalBiosRecovery:SetupVmediaLocal | [FSM:STAGE:FAILED¦RETRY]: Provisioning a V-Media device with a bootable BIOS image for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:SetupVmediaLocal) | warning | setup-vmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoverySetupVmediaLocal
F16984 | fsmStFailComputePhysicalBiosRecovery:SetupVmediaPeer | [FSM:STAGE:FAILED¦RETRY]: Provisioning a V-Media device with a bootable BIOS image for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:SetupVmediaPeer) | warning | setup-vmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoverySetupVmediaPeer
F16984 | fsmStFailComputePhysicalBiosRecovery:Shutdown | [FSM:STAGE:FAILED¦RETRY]: Shutting down server [dn] to prepare for BIOS recovery(FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Shutdown) | warning | shutdown-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoveryShutdown
F16984 | fsmStFailComputePhysicalBiosRecovery:Start | [FSM:STAGE:FAILED¦RETRY]: Running BIOS recovery on server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Start) | warning | start-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoveryStart
F16984 | fsmStFailComputePhysicalBiosRecovery:StopVMediaLocal | [FSM:STAGE:FAILED¦RETRY]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:StopVMediaLocal) | warning | stopvmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoveryStopVMediaLocal
F16984 | fsmStFailComputePhysicalBiosRecovery:StopVMediaPeer | [FSM:STAGE:FAILED¦RETRY]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:StopVMediaPeer) | warning | stopvmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoveryStopVMediaPeer
F16984 | fsmStFailComputePhysicalBiosRecovery:TeardownVmediaLocal | [FSM:STAGE:FAILED¦RETRY]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:TeardownVmediaLocal) | warning | teardown-vmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoveryTeardownVmediaLocal
F16984 | fsmStFailComputePhysicalBiosRecovery:TeardownVmediaPeer | [FSM:STAGE:FAILED¦RETRY]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:TeardownVmediaPeer) | warning | teardown-vmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoveryTeardownVmediaPeer
F16984 | fsmStFailComputePhysicalBiosRecovery:Wait | [FSM:STAGE:FAILED¦RETRY]: Waiting for completion of BIOS recovery for server [dn] (up to 15 min)(FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Wait) | warning | wait-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16984 | fsmStFailComputePhysicalBiosRecoveryWait
F16986 | fsmStFailComputePhysicalCmosReset:BladePowerOn | [FSM:STAGE:FAILED¦RETRY]: Power on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:BladePowerOn) | warning | blade-power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16986 | fsmStFailComputePhysicalCmosResetBladePowerOn
F16986 | fsmStFailComputePhysicalCmosReset:Execute | [FSM:STAGE:FAILED¦RETRY]: Resetting CMOS for server [serverId](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16986 | fsmStFailComputePhysicalCmosResetExecute
F16986 | fsmStFailComputePhysicalCmosReset:PreSanitize | [FSM:STAGE:FAILED¦RETRY]: Preparing to check hardware configuration server [serverId](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16986 | fsmStFailComputePhysicalCmosResetPreSanitize
F16986 | fsmStFailComputePhysicalCmosReset:ReconfigBios | [FSM:STAGE:FAILED¦RETRY]: Reconfiguring BIOS Settings and Boot Order of server [serverId] for service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:ReconfigBios) | warning | reconfig-bios-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16986 | fsmStFailComputePhysicalCmosResetReconfigBios
F16986 | fsmStFailComputePhysicalCmosReset:ReconfigUuid | [FSM:STAGE:FAILED¦RETRY]: Reconfiguring logical UUID of server [serverId] for service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:ReconfigUuid) | warning | reconfig-uuid-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16986 | fsmStFailComputePhysicalCmosResetReconfigUuid
F16986 | fsmStFailComputePhysicalCmosReset:Sanitize | [FSM:STAGE:FAILED¦RETRY]: Checking hardware configuration server [serverId](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16986 | fsmStFailComputePhysicalCmosResetSanitize
F16987 | fsmStFailComputePhysicalResetBmc:Execute | [FSM:STAGE:FAILED¦RETRY]: Resetting Management Controller on server [dn](FSM-STAGE:sam:dme:ComputePhysicalResetBmc:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 16987 | fsmStFailComputePhysicalResetBmcExecute
F16988 | fsmStFailEquipmentIOCardResetIom:Execute | [FSM:STAGE:FAILED¦RETRY]: Reset IOM [id] on Fex [chassisId](FSM-STAGE:sam:dme:EquipmentIOCardResetIom:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 16988 | fsmStFailEquipmentIOCardResetIomExecute
F17008 | fsmStFailComputePhysicalUpdateExtUsers:Deploy | [FSM:STAGE:FAILED¦RETRY]: external mgmt user deployment on server [dn] (profile [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalUpdateExtUsers:Deploy) | warning | deploy-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17008 | fsmStFailComputePhysicalUpdateExtUsersDeploy
F17012 | fsmStFailSysdebugTechSupportInitiate:Local | [FSM:STAGE:FAILED¦RETRY]: create tech-support file from GUI on local(FSM-STAGE:sam:dme:SysdebugTechSupportInitiate:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 17012 | fsmStFailSysdebugTechSupportInitiateLocal
F17013 | fsmStFailSysdebugTechSupportDeleteTechSupFile:Local | [FSM:STAGE:FAILED¦RETRY]: delete tech-support file from GUI on local(FSM-STAGE:sam:dme:SysdebugTechSupportDeleteTechSupFile:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 17013 | fsmStFailSysdebugTechSupportDeleteTechSupFileLocal
F17013 | fsmStFailSysdebugTechSupportDeleteTechSupFile:peer | [FSM:STAGE:FAILED¦RETRY]: delete tech-support file from GUI on peer(FSM-STAGE:sam:dme:SysdebugTechSupportDeleteTechSupFile:peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 17013 | fsmStFailSysdebugTechSupportDeleteTechSupFilePeer
F17014 | fsmStFailFirmwareDownloaderDownload:CopyRemote | [FSM:STAGE:FAILED¦RETRY]: sync images to subordinate(FSM-STAGE:sam:dme:FirmwareDownloaderDownload:CopyRemote) | warning | copy-remote-failed | None set. | None set. | none | TRUE | fsm | firmware:Downloader | sys/fw-catalogue/dnld-[fileName] | 17014 | fsmStFailFirmwareDownloaderDownloadCopyRemote
F17014 | fsmStFailFirmwareDownloaderDownload:DeleteLocal | [FSM:STAGE:FAILED¦RETRY]: deleting downloadable [fileName] on local(FSM-STAGE:sam:dme:FirmwareDownloaderDownload:DeleteLocal) | warning | delete-local-failed | None set. | None set. | none | TRUE | fsm | firmware:Downloader | sys/fw-catalogue/dnld-[fileName] | 17014 | fsmStFailFirmwareDownloaderDownloadDeleteLocal
F17014 | fsmStFailFirmwareDownloaderDownload:Local | [FSM:STAGE:FAILED¦RETRY]: downloading image [fileName] from [server](FSM-STAGE:sam:dme:FirmwareDownloaderDownload:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | firmware:Downloader | sys/fw-catalogue/dnld-[fileName] | 17014 | fsmStFailFirmwareDownloaderDownloadLocal
F17014 | fsmStFailFirmwareDownloaderDownload:UnpackLocal | [FSM:STAGE:FAILED¦RETRY]: unpacking image [fileName] on primary(FSM-STAGE:sam:dme:FirmwareDownloaderDownload:UnpackLocal) | warning | unpack-local-failed | None set. | None set. | none | TRUE | fsm | firmware:Downloader | sys/fw-catalogue/dnld-[fileName] | 17014 | fsmStFailFirmwareDownloaderDownloadUnpackLocal
F17014 | fsmStFailLicenseDownloaderDownload:CopyRemote | [FSM:STAGE:FAILED¦RETRY]: Copy the license file to subordinate for inventory(FSM-STAGE:sam:dme:LicenseDownloaderDownload:CopyRemote) | warning | copy-remote-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 17014 | fsmStFailLicenseDownloaderDownloadCopyRemote
F17014 | fsmStFailLicenseDownloaderDownload:DeleteLocal | [FSM:STAGE:FAILED¦RETRY]: deleting temporary files for [fileName] on local(FSM-STAGE:sam:dme:LicenseDownloaderDownload:DeleteLocal) | warning | delete-local-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 17014 | fsmStFailLicenseDownloaderDownloadDeleteLocal
F17014 | fsmStFailLicenseDownloaderDownload:DeleteRemote | [FSM:STAGE:FAILED¦RETRY]: deleting temporary files for [fileName] on subordinate(FSM-STAGE:sam:dme:LicenseDownloaderDownload:DeleteRemote) | warning | delete-remote-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 17014 | fsmStFailLicenseDownloaderDownloadDeleteRemote
F17014 | fsmStFailLicenseDownloaderDownload:Local | [FSM:STAGE:FAILED¦RETRY]: downloading license file [fileName] from [server](FSM-STAGE:sam:dme:LicenseDownloaderDownload:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 17014 | fsmStFailLicenseDownloaderDownloadLocal
F17014 | fsmStFailLicenseDownloaderDownload:ValidateLocal | [FSM:STAGE:FAILED¦RETRY]: validation for license file [fileName] on primary(FSM-STAGE:sam:dme:LicenseDownloaderDownload:ValidateLocal) | warning | validate-local-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 17014 | fsmStFailLicenseDownloaderDownloadValidateLocal
F17014 | fsmStFailLicenseDownloaderDownload:ValidateRemote | [FSM:STAGE:FAILED¦RETRY]: validation for license file [fileName] on subordinate(FSM-STAGE:sam:dme:LicenseDownloaderDownload:ValidateRemote) | warning | validate-remote-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 17014 | fsmStFailLicenseDownloaderDownloadValidateRemote
F17014 | fsmStFailSysdebugCoreDownload:CopyPrimary | [FSM:STAGE:FAILED¦RETRY]: Copy the Core file to primary for download(FSM-STAGE:sam:dme:SysdebugCoreDownload:CopyPrimary) | warning | copy-primary-failed | None set. | None set. | none | TRUE | fsm | sysdebug:Core | sys/corefiles/file-[name]¦[switchId] | 17014 | fsmStFailSysdebugCoreDownloadCopyPrimary
F17014 | fsmStFailSysdebugCoreDownload:CopySub | [FSM:STAGE:FAILED¦RETRY]: copy Core file on subordinate switch to tmp directory(FSM-STAGE:sam:dme:SysdebugCoreDownload:CopySub) | warning | copy-sub-failed | None set. | None set. | none | TRUE | fsm | sysdebug:Core | sys/corefiles/file-[name]¦[switchId] | 17014 | fsmStFailSysdebugCoreDownloadCopySub
F17014 | fsmStFailSysdebugCoreDownload:DeletePrimary | [FSM:STAGE:FAILED¦RETRY]: Delete the Core file from primary switch under tmp directory(FSM-STAGE:sam:dme:SysdebugCoreDownload:DeletePrimary) | warning | delete-primary-failed | None set. | None set. | none | TRUE | fsm | sysdebug:Core | sys/corefiles/file-[name]¦[switchId] | 17014 | fsmStFailSysdebugCoreDownloadDeletePrimary
F17014 | fsmStFailSysdebugCoreDownload:DeleteSub | [FSM:STAGE:FAILED¦RETRY]: Delete the Core file from subordinate under tmp directory(FSM-STAGE:sam:dme:SysdebugCoreDownload:DeleteSub) | warning | delete-sub-failed | None set. | None set. | none | TRUE | fsm | sysdebug:Core | sys/corefiles/file-[name]¦[switchId] | 17014 | fsmStFailSysdebugCoreDownloadDeleteSub
F17014 | fsmStFailSysdebugTechSupportDownload:CopyPrimary | [FSM:STAGE:FAILED¦RETRY]: Copy the tech-support file to primary for download(FSM-STAGE:sam:dme:SysdebugTechSupportDownload:CopyPrimary) | warning | copy-primary-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 17014 | fsmStFailSysdebugTechSupportDownloadCopyPrimary
F17014 | fsmStFailSysdebugTechSupportDownload:CopySub | [FSM:STAGE:FAILED¦RETRY]: copy tech-support file on subordinate switch to tmp directory(FSM-STAGE:sam:dme:SysdebugTechSupportDownload:CopySub) | warning | copy-sub-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 17014 | fsmStFailSysdebugTechSupportDownloadCopySub
F17014 | fsmStFailSysdebugTechSupportDownload:DeletePrimary | [FSM:STAGE:FAILED¦RETRY]: Delete the tech-support file from primary switch under tmp directory(FSM-STAGE:sam:dme:SysdebugTechSupportDownload:DeletePrimary) | warning | delete-primary-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 17014 | fsmStFailSysdebugTechSupportDownloadDeletePrimary
F17014 | fsmStFailSysdebugTechSupportDownload:DeleteSub | [FSM:STAGE:FAILED¦RETRY]: Delete the tech-support file from subordinate under tmp directory(FSM-STAGE:sam:dme:SysdebugTechSupportDownload:DeleteSub) | warning | delete-sub-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 17014 | fsmStFailSysdebugTechSupportDownloadDeleteSub
F17043 | fsmStFailComputePhysicalUpdateAdaptor:PollUpdateStatusLocal | [FSM:STAGE:FAILED¦RETRY]: waiting for update to complete(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:PollUpdateStatusLocal) | warning | poll-update-status-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17043 | fsmStFailComputePhysicalUpdateAdaptorPollUpdateStatusLocal
F17043 | fsmStFailComputePhysicalUpdateAdaptor:PollUpdateStatusPeer | [FSM:STAGE:FAILED¦RETRY]: waiting for update to complete(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:PollUpdateStatusPeer) | warning | poll-update-status-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17043 | fsmStFailComputePhysicalUpdateAdaptorPollUpdateStatusPeer
F17043 | fsmStFailComputePhysicalUpdateAdaptor:PowerOff | [FSM:STAGE:FAILED¦RETRY]: Power off the server(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:PowerOff) | warning | power-off-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17043 | fsmStFailComputePhysicalUpdateAdaptorPowerOff
F17043 | fsmStFailComputePhysicalUpdateAdaptor:PowerOn | [FSM:STAGE:FAILED¦RETRY]: power on the blade(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:PowerOn) | warning | power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17043 | fsmStFailComputePhysicalUpdateAdaptorPowerOn
F17043 | fsmStFailComputePhysicalUpdateAdaptor:UpdateRequestLocal | [FSM:STAGE:FAILED¦RETRY]: sending update request to Adaptor(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:UpdateRequestLocal) | warning | update-request-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17043 | fsmStFailComputePhysicalUpdateAdaptorUpdateRequestLocal
F17043 | fsmStFailComputePhysicalUpdateAdaptor:UpdateRequestPeer | [FSM:STAGE:FAILED¦RETRY]: sending update request to Adaptor(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:UpdateRequestPeer) | warning | update-request-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17043 | fsmStFailComputePhysicalUpdateAdaptorUpdateRequestPeer
F17044 | fsmStFailComputePhysicalActivateAdaptor:ActivateLocal | [FSM:STAGE:FAILED¦RETRY]: activating backup image of Adaptor(FSM-STAGE:sam:dme:ComputePhysicalActivateAdaptor:ActivateLocal) | warning | activate-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17044 | fsmStFailComputePhysicalActivateAdaptorActivateLocal
F17044 | fsmStFailComputePhysicalActivateAdaptor:ActivatePeer | [FSM:STAGE:FAILED¦RETRY]: activating backup image of Adaptor(FSM-STAGE:sam:dme:ComputePhysicalActivateAdaptor:ActivatePeer) | warning | activate-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17044 | fsmStFailComputePhysicalActivateAdaptorActivatePeer
F17044 | fsmStFailComputePhysicalActivateAdaptor:PowerOn | [FSM:STAGE:FAILED¦RETRY]: power on the blade(FSM-STAGE:sam:dme:ComputePhysicalActivateAdaptor:PowerOn) | warning | power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17044 | fsmStFailComputePhysicalActivateAdaptorPowerOn
F17044 | fsmStFailComputePhysicalActivateAdaptor:Reset | [FSM:STAGE:FAILED¦RETRY]: reseting the blade(FSM-STAGE:sam:dme:ComputePhysicalActivateAdaptor:Reset) | warning | reset-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17044 | fsmStFailComputePhysicalActivateAdaptorReset
F17045 | fsmStFailCapabilityCatalogueActivateCatalog:ApplyCatalog | [FSM:STAGE:FAILED¦RETRY]: applying changes to catalog(FSM-STAGE:sam:dme:CapabilityCatalogueActivateCatalog:ApplyCatalog) | warning | apply-catalog-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 17045 | fsmStFailCapabilityCatalogueActivateCatalogApplyCatalog
F17045 | fsmStFailCapabilityCatalogueActivateCatalog:CopyRemote | [FSM:STAGE:FAILED¦RETRY]: syncing catalog changes to subordinate(FSM-STAGE:sam:dme:CapabilityCatalogueActivateCatalog:CopyRemote) | warning | copy-remote-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 17045 | fsmStFailCapabilityCatalogueActivateCatalogCopyRemote
F17045 | fsmStFailCapabilityCatalogueActivateCatalog:EvaluateStatus | [FSM:STAGE:FAILED¦RETRY]: evaluating status of activation(FSM-STAGE:sam:dme:CapabilityCatalogueActivateCatalog:EvaluateStatus) | warning | evaluate-status-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 17045 | fsmStFailCapabilityCatalogueActivateCatalogEvaluateStatus
F17045 | fsmStFailCapabilityCatalogueActivateCatalog:RescanImages | [FSM:STAGE:FAILED¦RETRY]: rescanning image files(FSM-STAGE:sam:dme:CapabilityCatalogueActivateCatalog:RescanImages) | warning | rescan-images-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 17045 | fsmStFailCapabilityCatalogueActivateCatalogRescanImages
F17045 | fsmStFailCapabilityCatalogueActivateCatalog:UnpackLocal | [FSM:STAGE:FAILED¦RETRY]: activating catalog changes(FSM-STAGE:sam:dme:CapabilityCatalogueActivateCatalog:UnpackLocal) | warning | unpack-local-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 17045 | fsmStFailCapabilityCatalogueActivateCatalogUnpackLocal
F17046 | fsmStFailCapabilityMgmtExtensionActivateMgmtExt:ApplyCatalog | [FSM:STAGE:FAILED¦RETRY]: applying changes to catalog(FSM-STAGE:sam:dme:CapabilityMgmtExtensionActivateMgmtExt:ApplyCatalog) | warning | apply-catalog-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 17046 | fsmStFailCapabilityMgmtExtensionActivateMgmtExtApplyCatalog
F17046 | fsmStFailCapabilityMgmtExtensionActivateMgmtExt:CopyRemote | [FSM:STAGE:FAILED¦RETRY]: syncing management extension changes to subordinate(FSM-STAGE:sam:dme:CapabilityMgmtExtensionActivateMgmtExt:CopyRemote) | warning | copy-remote-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 17046 | fsmStFailCapabilityMgmtExtensionActivateMgmtExtCopyRemote
F17046 | fsmStFailCapabilityMgmtExtensionActivateMgmtExt:EvaluateStatus | [FSM:STAGE:FAILED¦RETRY]: evaluating status of activation(FSM-STAGE:sam:dme:CapabilityMgmtExtensionActivateMgmtExt:EvaluateStatus) | warning | evaluate-status-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 17046 | fsmStFailCapabilityMgmtExtensionActivateMgmtExtEvaluateStatus
F17046 | fsmStFailCapabilityMgmtExtensionActivateMgmtExt:RescanImages | [FSM:STAGE:FAILED¦RETRY]: rescanning image files(FSM-STAGE:sam:dme:CapabilityMgmtExtensionActivateMgmtExt:RescanImages) | warning | rescan-images-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 17046 | fsmStFailCapabilityMgmtExtensionActivateMgmtExtRescanImages
F17046 | fsmStFailCapabilityMgmtExtensionActivateMgmtExt:UnpackLocal | [FSM:STAGE:FAILED¦RETRY]: activating management extension changes(FSM-STAGE:sam:dme:CapabilityMgmtExtensionActivateMgmtExt:UnpackLocal) | warning | unpack-local-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 17046 | fsmStFailCapabilityMgmtExtensionActivateMgmtExtUnpackLocal
F17051 | fsmStFailLicenseFileInstall:Local | [FSM:STAGE:FAILED¦RETRY]: Installing license on primary(FSM-STAGE:sam:dme:LicenseFileInstall:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | license:File | sys/license/file-[scope]:[id] | 17051 | fsmStFailLicenseFileInstallLocal
F17051 | fsmStFailLicenseFileInstall:Remote | [FSM:STAGE:FAILED¦RETRY]: Installing license on subordinate(FSM-STAGE:sam:dme:LicenseFileInstall:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | license:File | sys/license/file-[scope]:[id] | 17051 | fsmStFailLicenseFileInstallRemote
F17052 | fsmStFailLicenseFileClear:Local | [FSM:STAGE:FAILED¦RETRY]: Clearing license on primary(FSM-STAGE:sam:dme:LicenseFileClear:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | license:File | sys/license/file-[scope]:[id] | 17052 | fsmStFailLicenseFileClearLocal
F17052 | fsmStFailLicenseFileClear:Remote | [FSM:STAGE:FAILED¦RETRY]: Clearing license on subordinate(FSM-STAGE:sam:dme:LicenseFileClear:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | license:File | sys/license/file-[scope]:[id] | 17052 | fsmStFailLicenseFileClearRemote
F17053 | fsmStFailLicenseInstanceUpdateFlexlm:Local | [FSM:STAGE:FAILED¦RETRY]: Updating on primary(FSM-STAGE:sam:dme:LicenseInstanceUpdateFlexlm:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 17053 | fsmStFailLicenseInstanceUpdateFlexlmLocal
F17053 | fsmStFailLicenseInstanceUpdateFlexlm:Remote | [FSM:STAGE:FAILED¦RETRY]: Updating on subordinate(FSM-STAGE:sam:dme:LicenseInstanceUpdateFlexlm:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 17053 | fsmStFailLicenseInstanceUpdateFlexlmRemote
F17083 | fsmStFailComputePhysicalConfigSoL:Execute | [FSM:STAGE:FAILED¦RETRY]: configuring SoL interface on server [dn](FSM-STAGE:sam:dme:ComputePhysicalConfigSoL:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17083 | fsmStFailComputePhysicalConfigSoLExecute
F17084 | fsmStFailComputePhysicalUnconfigSoL:Execute | [FSM:STAGE:FAILED¦RETRY]: removing SoL interface configuration from server [dn](FSM-STAGE:sam:dme:ComputePhysicalUnconfigSoL:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17084 | fsmStFailComputePhysicalUnconfigSoLExecute
F17089 | fsmStFailPortPIoInCompatSfpPresence:Shutdown | [FSM:STAGE:FAILED¦RETRY]: Shutting down port(FSM-STAGE:sam:dme:PortPIoInCompatSfpPresence:Shutdown) | warning | shutdown-failed | None set. | None set. | none | TRUE | fsm | port:PIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 17089 | fsmStFailPortPIoInCompatSfpPresenceShutdown
F17116 | fsmStFailComputePhysicalDiagnosticInterrupt:Execute | [FSM:STAGE:FAILED¦RETRY]: Execute Diagnostic Interrupt(NMI) for server [dn](FSM-STAGE:sam:dme:ComputePhysicalDiagnosticInterrupt:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17116 | fsmStFailComputePhysicalDiagnosticInterruptExecute
F17134 | fsmStFailEquipmentChassisDynamicReallocation:Config | [FSM:STAGE:FAILED¦RETRY]: (FSM-STAGE:sam:dme:EquipmentChassisDynamicReallocation:Config) | warning | config-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 17134 | fsmStFailEquipmentChassisDynamicReallocationConfig
F17163 | fsmStFailComputePhysicalResetKvm:Execute | [FSM:STAGE:FAILED¦RETRY]: Execute KVM Reset for server [dn](FSM-STAGE:sam:dme:ComputePhysicalResetKvm:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17163 | fsmStFailComputePhysicalResetKvmExecute
F17169 | fsmStFailMgmtControllerOnline:BmcConfigureConnLocal | [FSM:STAGE:FAILED¦RETRY]: Configuring connectivity on CIMC(FSM-STAGE:sam:dme:MgmtControllerOnline:BmcConfigureConnLocal) | warning | bmc-configure-conn-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 17169 | fsmStFailMgmtControllerOnlineBmcConfigureConnLocal
F17169 | fsmStFailMgmtControllerOnline:BmcConfigureConnPeer | [FSM:STAGE:FAILED¦RETRY]: Configuring connectivity on CIMC(FSM-STAGE:sam:dme:MgmtControllerOnline:BmcConfigureConnPeer) | warning | bmc-configure-conn-peer-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 17169 | fsmStFailMgmtControllerOnlineBmcConfigureConnPeer
F17169 | fsmStFailMgmtControllerOnline:SwConfigureConnLocal | [FSM:STAGE:FAILED¦RETRY]: Configuring fabric-interconnect connectivity to CIMC(FSM-STAGE:sam:dme:MgmtControllerOnline:SwConfigureConnLocal) | warning | sw-configure-conn-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 17169 | fsmStFailMgmtControllerOnlineSwConfigureConnLocal
F17169 | fsmStFailMgmtControllerOnline:SwConfigureConnPeer | [FSM:STAGE:FAILED¦RETRY]: Configuring fabric-interconnect connectivity to CIMC(FSM-STAGE:sam:dme:MgmtControllerOnline:SwConfigureConnPeer) | warning | sw-configure-conn-peer-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 17169 | fsmStFailMgmtControllerOnlineSwConfigureConnPeer
F17170 | fsmStFailComputeRackUnitOffline:CleanupLocal | [FSM:STAGE:FAILED¦RETRY]: cleaning host entries on local fabric-interconnect(FSM-STAGE:sam:dme:ComputeRackUnitOffline:CleanupLocal) | warning | cleanup-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 17170 | fsmStFailComputeRackUnitOfflineCleanupLocal
F17170 | fsmStFailComputeRackUnitOffline:CleanupPeer | [FSM:STAGE:FAILED¦RETRY]: cleaning host entries on peer fabric-interconnect(FSM-STAGE:sam:dme:ComputeRackUnitOffline:CleanupPeer) | warning | cleanup-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 17170 | fsmStFailComputeRackUnitOfflineCleanupPeer
F17170 | fsmStFailComputeRackUnitOffline:SwUnconfigureLocal | [FSM:STAGE:FAILED¦RETRY]: Unconfiguring fabric-interconnect connectivity to CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitOffline:SwUnconfigureLocal) | warning | sw-unconfigure-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 17170 | fsmStFailComputeRackUnitOfflineSwUnconfigureLocal
F17170 | fsmStFailComputeRackUnitOffline:SwUnconfigurePeer | [FSM:STAGE:FAILED¦RETRY]: Unconfiguring fabric-interconnect connectivity to CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitOffline:SwUnconfigurePeer) | warning | sw-unconfigure-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 17170 | fsmStFailComputeRackUnitOfflineSwUnconfigurePeer
F17187 | fsmStFailEquipmentLocatorLedSetFiLocatorLed:Execute | [FSM:STAGE:FAILED¦RETRY]: setting FI locator led to [adminState](FSM-STAGE:sam:dme:EquipmentLocatorLedSetFiLocatorLed:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:LocatorLed | sys/chassis-[id]/blade-[slotId]/locator-led | 17187 | fsmStFailEquipmentLocatorLedSetFiLocatorLedExecute
F17223 | fsmStFailVnicProfileSetDeployAlias:Local | [FSM:STAGE:FAILED¦RETRY]: VNIC profile alias configuration on local fabric(FSM-STAGE:sam:dme:VnicProfileSetDeployAlias:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | vnic:ProfileSet | fabric/lan/profiles | 17223 | fsmStFailVnicProfileSetDeployAliasLocal
F17223 | fsmStFailVnicProfileSetDeployAlias:Peer | [FSM:STAGE:FAILED¦RETRY]: VNIC profile alias configuration on peer fabric(FSM-STAGE:sam:dme:VnicProfileSetDeployAlias:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | vnic:ProfileSet | fabric/lan/profiles | 17223 | fsmStFailVnicProfileSetDeployAliasPeer
F17239 | fsmStFailSwPhysConfPhysical:ConfigSwA | [FSM:STAGE:FAILED¦RETRY]: Configure physical port types on fabric interconnect [id](FSM-STAGE:sam:dme:SwPhysConfPhysical:ConfigSwA) | warning | config-sw-afailed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 17239 | fsmStFailSwPhysConfPhysicalConfigSwA
F17239 | fsmStFailSwPhysConfPhysical:ConfigSwB | [FSM:STAGE:FAILED¦RETRY]: Configure physical port types on fabric interconnect [id](FSM-STAGE:sam:dme:SwPhysConfPhysical:ConfigSwB) | warning | config-sw-bfailed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 17239 | fsmStFailSwPhysConfPhysicalConfigSwB
F17239 | fsmStFailSwPhysConfPhysical:PortInventorySwA | [FSM:STAGE:FAILED¦RETRY]: Performing local port inventory of switch [id](FSM-STAGE:sam:dme:SwPhysConfPhysical:PortInventorySwA) | warning | port-inventory-sw-afailed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 17239 | fsmStFailSwPhysConfPhysicalPortInventorySwA
F17239 | fsmStFailSwPhysConfPhysical:PortInventorySwB | [FSM:STAGE:FAILED¦RETRY]: Performing peer port inventory of switch [id](FSM-STAGE:sam:dme:SwPhysConfPhysical:PortInventorySwB) | warning | port-inventory-sw-bfailed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 17239 | fsmStFailSwPhysConfPhysicalPortInventorySwB
F17239 | fsmStFailSwPhysConfPhysical:VerifyPhysConfig | [FSM:STAGE:FAILED¦RETRY]: Verifying physical transition on fabric interconnect [id](FSM-STAGE:sam:dme:SwPhysConfPhysical:VerifyPhysConfig) | warning | verify-phys-config-failed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 17239 | fsmStFailSwPhysConfPhysicalVerifyPhysConfig
F17254 | fsmStFailExtvmmEpClusterRole:SetLocal | [FSM:STAGE:FAILED¦RETRY]: external VM management cluster role configuration on local fabric(FSM-STAGE:sam:dme:ExtvmmEpClusterRole:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | extvmm:Ep | sys/extvm-mgmt | 17254 | fsmStFailExtvmmEpClusterRoleSetLocal
F17254 | fsmStFailExtvmmEpClusterRole:SetPeer | [FSM:STAGE:FAILED¦RETRY]: external VM management cluster role configuration on peer fabric(FSM-STAGE:sam:dme:ExtvmmEpClusterRole:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | extvmm:Ep | sys/extvm-mgmt | 17254 | fsmStFailExtvmmEpClusterRoleSetPeer
F17262 | fsmStFailEquipmentBeaconLedIlluminate:ExecuteA | [FSM:STAGE:FAILED¦RETRY]: Turn beacon lights on/off for [dn] on fabric interconnect [id](FSM-STAGE:sam:dme:EquipmentBeaconLedIlluminate:ExecuteA) | warning | execute-afailed | None set. | None set. | none | TRUE | fsm | equipment:BeaconLed | sys/chassis-[id]/blade-[slotId]/beacon | 17262 | fsmStFailEquipmentBeaconLedIlluminateExecuteA
F17262 | fsmStFailEquipmentBeaconLedIlluminate:ExecuteB | [FSM:STAGE:FAILED¦RETRY]: Turn beacon lights on/off for [dn] on fabric interconnect [id](FSM-STAGE:sam:dme:EquipmentBeaconLedIlluminate:ExecuteB) | warning | execute-bfailed | None set. | None set. | none | TRUE | fsm | equipment:BeaconLed | sys/chassis-[id]/blade-[slotId]/beacon | 17262 | fsmStFailEquipmentBeaconLedIlluminateExecuteB
F17271 | fsmStFailEtherServerIntFIoConfigSpeed:Configure | [FSM:STAGE:FAILED¦RETRY]: Configure admin speed for [dn](FSM-STAGE:sam:dme:EtherServerIntFIoConfigSpeed:Configure) | warning | configure-failed | None set. | None set. | none | TRUE | fsm | ether:ServerIntFIo | sys/chassis-[id]/blade-[slotId]/diag/port-[portId] | 17271 | fsmStFailEtherServerIntFIoConfigSpeedConfigure
F17281 | fsmStFailComputePhysicalUpdateBIOS:Clear | [FSM:STAGE:FAILED¦RETRY]: clearing pending BIOS image update(FSM-STAGE:sam:dme:ComputePhysicalUpdateBIOS:Clear) | warning | clear-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17281 | fsmStFailComputePhysicalUpdateBIOSClear
F17281 | fsmStFailComputePhysicalUpdateBIOS:PollClearStatus | [FSM:STAGE:FAILED¦RETRY]: waiting for pending BIOS image update to clear(FSM-STAGE:sam:dme:ComputePhysicalUpdateBIOS:PollClearStatus) | warning | poll-clear-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17281 | fsmStFailComputePhysicalUpdateBIOSPollClearStatus
F17281 | fsmStFailComputePhysicalUpdateBIOS:PollUpdateStatus | [FSM:STAGE:FAILED¦RETRY]: waiting for BIOS update to complete(FSM-STAGE:sam:dme:ComputePhysicalUpdateBIOS:PollUpdateStatus) | warning | poll-update-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17281 | fsmStFailComputePhysicalUpdateBIOSPollUpdateStatus
F17281 | fsmStFailComputePhysicalUpdateBIOS:UpdateRequest | [FSM:STAGE:FAILED¦RETRY]: sending BIOS update request to CIMC(FSM-STAGE:sam:dme:ComputePhysicalUpdateBIOS:UpdateRequest) | warning | update-request-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17281 | fsmStFailComputePhysicalUpdateBIOSUpdateRequest
F17282 | fsmStFailComputePhysicalActivateBIOS:Activate | [FSM:STAGE:FAILED¦RETRY]: activating BIOS image(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:Activate) | warning | activate-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17282 | fsmStFailComputePhysicalActivateBIOSActivate
F17282 | fsmStFailComputePhysicalActivateBIOS:Clear | [FSM:STAGE:FAILED¦RETRY]: clearing pending BIOS image activate(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:Clear) | warning | clear-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17282 | fsmStFailComputePhysicalActivateBIOSClear
F17282 | fsmStFailComputePhysicalActivateBIOS:PollActivateStatus | [FSM:STAGE:FAILED¦RETRY]: waiting for BIOS activate(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:PollActivateStatus) | warning | poll-activate-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17282 | fsmStFailComputePhysicalActivateBIOSPollActivateStatus
F17282 | fsmStFailComputePhysicalActivateBIOS:PollClearStatus | [FSM:STAGE:FAILED¦RETRY]: waiting for pending BIOS image activate to clear(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:PollClearStatus) | warning | poll-clear-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17282 | fsmStFailComputePhysicalActivateBIOSPollClearStatus
F17282 | fsmStFailComputePhysicalActivateBIOS:PowerOff | [FSM:STAGE:FAILED¦RETRY]: Power off the server(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:PowerOff) | warning | power-off-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17282 | fsmStFailComputePhysicalActivateBIOSPowerOff
F17282 | fsmStFailComputePhysicalActivateBIOS:PowerOn | [FSM:STAGE:FAILED¦RETRY]: power on the server(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:PowerOn) | warning | power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17282 | fsmStFailComputePhysicalActivateBIOSPowerOn
F17282 | fsmStFailComputePhysicalActivateBIOS:UpdateTokens | [FSM:STAGE:FAILED¦RETRY]: updating BIOS tokens(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:UpdateTokens) | warning | update-tokens-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 17282 | fsmStFailComputePhysicalActivateBIOSUpdateTokens
F77845 | fsmRmtErrEquipmentIOCardFePresence:CheckLicense | [FSM:STAGE:REMOTE-ERROR]: Checking license for chassis [chassisId] (iom [id])(FSM-STAGE:sam:dme:EquipmentIOCardFePresence:CheckLicense) | warning | check-license-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 77845 | fsmRmtErrEquipmentIOCardFePresenceCheckLicense
F77845 | fsmRmtErrEquipmentIOCardFePresence:Identify | [FSM:STAGE:REMOTE-ERROR]: identifying IOM [chassisId]/[id](FSM-STAGE:sam:dme:EquipmentIOCardFePresence:Identify) | warning | identify-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 77845 | fsmRmtErrEquipmentIOCardFePresenceIdentify
F77846 | fsmRmtErrEquipmentIOCardFeConn:ConfigureEndPoint | [FSM:STAGE:REMOTE-ERROR]: configuring management identity to IOM [chassisId]/[id]([side])(FSM-STAGE:sam:dme:EquipmentIOCardFeConn:ConfigureEndPoint) | warning | configure-end-point-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 77846 | fsmRmtErrEquipmentIOCardFeConnConfigureEndPoint
F77846 | fsmRmtErrEquipmentIOCardFeConn:ConfigureSwMgmtEndPoint | [FSM:STAGE:REMOTE-ERROR]: configuring fabric interconnect [switchId] mgmt connectivity to IOM [chassisId]/[id]([side])(FSM-STAGE:sam:dme:EquipmentIOCardFeConn:ConfigureSwMgmtEndPoint) | warning | configure-sw-mgmt-end-point-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 77846 | fsmRmtErrEquipmentIOCardFeConnConfigureSwMgmtEndPoint
F77846 | fsmRmtErrEquipmentIOCardFeConn:ConfigureVifNs | [FSM:STAGE:REMOTE-ERROR]: configuring IOM [chassisId]/[id]([side]) virtual name space(FSM-STAGE:sam:dme:EquipmentIOCardFeConn:ConfigureVifNs) | warning | configure-vif-ns-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 77846 | fsmRmtErrEquipmentIOCardFeConnConfigureVifNs
F77846 | fsmRmtErrEquipmentIOCardFeConn:DiscoverChassis | [FSM:STAGE:REMOTE-ERROR]: triggerring chassis discovery via IOM [chassisId]/[id]([side])(FSM-STAGE:sam:dme:EquipmentIOCardFeConn:DiscoverChassis) | warning | discover-chassis-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 77846 | fsmRmtErrEquipmentIOCardFeConnDiscoverChassis
F77846 | fsmRmtErrEquipmentIOCardFeConn:EnableChassis | [FSM:STAGE:REMOTE-ERROR]: enabling chassis [chassisId] on [side] side(FSM-STAGE:sam:dme:EquipmentIOCardFeConn:EnableChassis) | warning | enable-chassis-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 77846 | fsmRmtErrEquipmentIOCardFeConnEnableChassis
F77847 | fsmRmtErrEquipmentChassisRemoveChassis:DisableEndPoint | [FSM:STAGE:REMOTE-ERROR]: unconfiguring access to chassis [id](FSM-STAGE:sam:dme:EquipmentChassisRemoveChassis:DisableEndPoint) | warning | disable-end-point-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 77847 | fsmRmtErrEquipmentChassisRemoveChassisDisableEndPoint
F77847 | fsmRmtErrEquipmentChassisRemoveChassis:UnIdentifyLocal | [FSM:STAGE:REMOTE-ERROR]: erasing chassis identity [id] from primary(FSM-STAGE:sam:dme:EquipmentChassisRemoveChassis:UnIdentifyLocal) | warning | un-identify-local-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 77847 | fsmRmtErrEquipmentChassisRemoveChassisUnIdentifyLocal
F77847 | fsmRmtErrEquipmentChassisRemoveChassis:UnIdentifyPeer | [FSM:STAGE:REMOTE-ERROR]: erasing chassis identity [id] from secondary(FSM-STAGE:sam:dme:EquipmentChassisRemoveChassis:UnIdentifyPeer) | warning | un-identify-peer-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 77847 | fsmRmtErrEquipmentChassisRemoveChassisUnIdentifyPeer
F77847 | fsmRmtErrEquipmentChassisRemoveChassis:Wait | [FSM:STAGE:REMOTE-ERROR]: waiting for clean up of resources for chassis [id] (approx. 2 min)(FSM-STAGE:sam:dme:EquipmentChassisRemoveChassis:Wait) | warning | wait-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 77847 | fsmRmtErrEquipmentChassisRemoveChassisWait
F77847 | fsmRmtErrEquipmentChassisRemoveChassis:decomission | [FSM:STAGE:REMOTE-ERROR]: decomissioning chassis [id](FSM-STAGE:sam:dme:EquipmentChassisRemoveChassis:decomission) | warning | decomission-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 77847 | fsmRmtErrEquipmentChassisRemoveChassisDecomission
F77848 | fsmRmtErrEquipmentLocatorLedSetLocatorLed:Execute | [FSM:STAGE:REMOTE-ERROR]: setting locator led to [adminState](FSM-STAGE:sam:dme:EquipmentLocatorLedSetLocatorLed:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:LocatorLed | sys/chassis-[id]/blade-[slotId]/locator-led | 77848 | fsmRmtErrEquipmentLocatorLedSetLocatorLedExecute
F77958 | fsmRmtErrMgmtControllerExtMgmtIfConfig:Primary | [FSM:STAGE:REMOTE-ERROR]: external mgmt interface configuration on primary(FSM-STAGE:sam:dme:MgmtControllerExtMgmtIfConfig:Primary) | warning | primary-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 77958 | fsmRmtErrMgmtControllerExtMgmtIfConfigPrimary
F77958 | fsmRmtErrMgmtControllerExtMgmtIfConfig:Secondary | [FSM:STAGE:REMOTE-ERROR]: external mgmt interface configuration on secondary(FSM-STAGE:sam:dme:MgmtControllerExtMgmtIfConfig:Secondary) | warning | secondary-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 77958 | fsmRmtErrMgmtControllerExtMgmtIfConfigSecondary
F77959 | fsmRmtErrFabricComputeSlotEpIdentify:ExecuteLocal | [FSM:STAGE:REMOTE-ERROR]: identifying a server in [chassisId]/[slotId] via CIMC(FSM-STAGE:sam:dme:FabricComputeSlotEpIdentify:ExecuteLocal) | warning | execute-local-failed | None set. | None set. | none | TRUE | fsm | fabric:ComputeSlotEp | fabric/server/chassis-[chassisId]/slot-[slotId] | 77959 | fsmRmtErrFabricComputeSlotEpIdentifyExecuteLocal
F77959 | fsmRmtErrFabricComputeSlotEpIdentify:ExecutePeer | [FSM:STAGE:REMOTE-ERROR]: identifying a server in [chassisId]/[slotId] via CIMC(FSM-STAGE:sam:dme:FabricComputeSlotEpIdentify:ExecutePeer) | warning | execute-peer-failed | None set. | None set. | none | TRUE | fsm | fabric:ComputeSlotEp | fabric/server/chassis-[chassisId]/slot-[slotId] | 77959 | fsmRmtErrFabricComputeSlotEpIdentifyExecutePeer
F77960 | fsmRmtErrComputeBladeDiscover:BiosPostCompletion | [FSM:STAGE:REMOTE-ERROR]: Waiting for BIOS POST completion from CIMC on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:BiosPostCompletion) | warning | bios-post-completion-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBiosPostCompletion
F77960 | fsmRmtErrComputeBladeDiscover:BladeBootPnuos | [FSM:STAGE:REMOTE-ERROR]: power server [chassisId]/[slotId] on with pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:BladeBootPnuos) | warning | blade-boot-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBladeBootPnuos
F77960 | fsmRmtErrComputeBladeDiscover:BladeBootWait | [FSM:STAGE:REMOTE-ERROR]: Waiting for system reset on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:BladeBootWait) | warning | blade-boot-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBladeBootWait
F77960 | fsmRmtErrComputeBladeDiscover:BladePowerOn | [FSM:STAGE:REMOTE-ERROR]: power on server [chassisId]/[slotId] for discovery(FSM-STAGE:sam:dme:ComputeBladeDiscover:BladePowerOn) | warning | blade-power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBladePowerOn
F77960 | fsmRmtErrComputeBladeDiscover:BladeReadSmbios | [FSM:STAGE:REMOTE-ERROR]: Waiting for SMBIOS table from CIMC on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:BladeReadSmbios) | warning | blade-read-smbios-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBladeReadSmbios
F77960 | fsmRmtErrComputeBladeDiscover:BmcConfigPnuOS | [FSM:STAGE:REMOTE-ERROR]: provisioning a bootable device with a bootable pre-boot image for server(FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcConfigPnuOS) | warning | bmc-config-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBmcConfigPnuOS
F77960 | fsmRmtErrComputeBladeDiscover:BmcInventory | [FSM:STAGE:REMOTE-ERROR]: getting inventory of server [chassisId]/[slotId] via CIMC(FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcInventory) | warning | bmc-inventory-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBmcInventory
F77960 | fsmRmtErrComputeBladeDiscover:BmcPreConfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcPreConfigPnuOSLocal) | warning | bmc-pre-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBmcPreConfigPnuOSLocal
F77960 | fsmRmtErrComputeBladeDiscover:BmcPreConfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcPreConfigPnuOSPeer) | warning | bmc-pre-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBmcPreConfigPnuOSPeer
F77960 | fsmRmtErrComputeBladeDiscover:BmcPresence | [FSM:STAGE:REMOTE-ERROR]: checking CIMC of server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcPresence) | warning | bmc-presence-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBmcPresence
F77960 | fsmRmtErrComputeBladeDiscover:BmcShutdownDiscovered | [FSM:STAGE:REMOTE-ERROR]: Shutdown the server [chassisId]/[slotId]; deep discovery completed(FSM-STAGE:sam:dme:ComputeBladeDiscover:BmcShutdownDiscovered) | warning | bmc-shutdown-discovered-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverBmcShutdownDiscovered
F77960 | fsmRmtErrComputeBladeDiscover:ConfigFeLocal | [FSM:STAGE:REMOTE-ERROR]: configuring primary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:ConfigFeLocal) | warning | config-fe-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverConfigFeLocal
F77960 | fsmRmtErrComputeBladeDiscover:ConfigFePeer | [FSM:STAGE:REMOTE-ERROR]: configuring secondary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:ConfigFePeer) | warning | config-fe-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverConfigFePeer
F77960 | fsmRmtErrComputeBladeDiscover:ConfigUserAccess | [FSM:STAGE:REMOTE-ERROR]: configuring external user access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:ConfigUserAccess) | warning | config-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverConfigUserAccess
F77960 | fsmRmtErrComputeBladeDiscover:HandlePooling | [FSM:STAGE:REMOTE-ERROR]: Invoke post-discovery policies on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:HandlePooling) | warning | handle-pooling-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverHandlePooling
F77960 | fsmRmtErrComputeBladeDiscover:NicConfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: configure primary adapter in [chassisId]/[slotId] for pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:NicConfigPnuOSLocal) | warning | nic-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverNicConfigPnuOSLocal
F77960 | fsmRmtErrComputeBladeDiscover:NicConfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: configure secondary adapter in [chassisId]/[slotId] for pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:NicConfigPnuOSPeer) | warning | nic-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverNicConfigPnuOSPeer
F77960 | fsmRmtErrComputeBladeDiscover:NicPresenceLocal | [FSM:STAGE:REMOTE-ERROR]: detect mezz cards in [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:NicPresenceLocal) | warning | nic-presence-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverNicPresenceLocal
F77960 | fsmRmtErrComputeBladeDiscover:NicPresencePeer | [FSM:STAGE:REMOTE-ERROR]: detect mezz cards in [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:NicPresencePeer) | warning | nic-presence-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverNicPresencePeer
F77960 | fsmRmtErrComputeBladeDiscover:NicUnconfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfigure adapter of server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:NicUnconfigPnuOSLocal) | warning | nic-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverNicUnconfigPnuOSLocal
F77960 | fsmRmtErrComputeBladeDiscover:NicUnconfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfigure adapter of server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:NicUnconfigPnuOSPeer) | warning | nic-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverNicUnconfigPnuOSPeer
F77960 | fsmRmtErrComputeBladeDiscover:PnuOSCatalog | [FSM:STAGE:REMOTE-ERROR]: Populate pre-boot catalog to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSCatalog) | warning | pnuoscatalog-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverPnuOSCatalog
F77960 | fsmRmtErrComputeBladeDiscover:PnuOSIdent | [FSM:STAGE:REMOTE-ERROR]: Identify pre-boot environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSIdent) | warning | pnuosident-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverPnuOSIdent
F77960 | fsmRmtErrComputeBladeDiscover:PnuOSInventory | [FSM:STAGE:REMOTE-ERROR]: Perform inventory of server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSInventory) | warning | pnuosinventory-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverPnuOSInventory
F77960 | fsmRmtErrComputeBladeDiscover:PnuOSPolicy | [FSM:STAGE:REMOTE-ERROR]: Populate pre-boot environment behavior policy to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSPolicy) | warning | pnuospolicy-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverPnuOSPolicy
F77960 | fsmRmtErrComputeBladeDiscover:PnuOSScrub | [FSM:STAGE:REMOTE-ERROR]: Scrub server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSScrub) | warning | pnuosscrub-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverPnuOSScrub
F77960 | fsmRmtErrComputeBladeDiscover:PnuOSSelfTest | [FSM:STAGE:REMOTE-ERROR]: Trigger self-test of server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:PnuOSSelfTest) | warning | pnuosself-test-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverPnuOSSelfTest
F77960 | fsmRmtErrComputeBladeDiscover:PreSanitize | [FSM:STAGE:REMOTE-ERROR]: Preparing to check hardware configuration server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverPreSanitize
F77960 | fsmRmtErrComputeBladeDiscover:Sanitize | [FSM:STAGE:REMOTE-ERROR]: Checking hardware configuration server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSanitize
F77960 | fsmRmtErrComputeBladeDiscover:SetupVmediaLocal | [FSM:STAGE:REMOTE-ERROR]: provisioning a Virtual Media device with a bootable pre-boot image for blade [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:SetupVmediaLocal) | warning | setup-vmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSetupVmediaLocal
F77960 | fsmRmtErrComputeBladeDiscover:SetupVmediaPeer | [FSM:STAGE:REMOTE-ERROR]: provisioning a Virtual Media device with a bootable pre-boot image for blade [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:SetupVmediaPeer) | warning | setup-vmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSetupVmediaPeer
F77960 | fsmRmtErrComputeBladeDiscover:SolRedirectDisable | [FSM:STAGE:REMOTE-ERROR]: Disable Sol Redirection on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:SolRedirectDisable) | warning | sol-redirect-disable-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSolRedirectDisable
F77960 | fsmRmtErrComputeBladeDiscover:SolRedirectEnable | [FSM:STAGE:REMOTE-ERROR]: set up bios token on server [chassisId]/[slotId] for Sol redirect(FSM-STAGE:sam:dme:ComputeBladeDiscover:SolRedirectEnable) | warning | sol-redirect-enable-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSolRedirectEnable
F77960 | fsmRmtErrComputeBladeDiscover:SwConfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: configure primary fabric interconnect in [chassisId]/[slotId] for pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:SwConfigPnuOSLocal) | warning | sw-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSwConfigPnuOSLocal
F77960 | fsmRmtErrComputeBladeDiscover:SwConfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: configure secondary fabric interconnect in [chassisId]/[slotId] for pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:SwConfigPnuOSPeer) | warning | sw-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSwConfigPnuOSPeer
F77960 | fsmRmtErrComputeBladeDiscover:SwUnconfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfigure primary fabric interconnect for server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:SwUnconfigPnuOSLocal) | warning | sw-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSwUnconfigPnuOSLocal
F77960 | fsmRmtErrComputeBladeDiscover:SwUnconfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfigure secondary fabric interconnect for server [chassisId]/[slotId] pre-boot environment(FSM-STAGE:sam:dme:ComputeBladeDiscover:SwUnconfigPnuOSPeer) | warning | sw-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSwUnconfigPnuOSPeer
F77960 | fsmRmtErrComputeBladeDiscover:TeardownVmediaLocal | [FSM:STAGE:REMOTE-ERROR]: unprovisioning the Virtual Media bootable device for blade [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:TeardownVmediaLocal) | warning | teardown-vmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverTeardownVmediaLocal
F77960 | fsmRmtErrComputeBladeDiscover:TeardownVmediaPeer | [FSM:STAGE:REMOTE-ERROR]: unprovisioning the Virtual media bootable device for blade [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:TeardownVmediaPeer) | warning | teardown-vmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverTeardownVmediaPeer
F77960 | fsmRmtErrComputeBladeDiscover:hagConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to pre-boot environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:hagConnect) | warning | hag-connect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverHagConnect
F77960 | fsmRmtErrComputeBladeDiscover:hagDisconnect | [FSM:STAGE:REMOTE-ERROR]: Disconnect pre-boot environment agent for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:hagDisconnect) | warning | hag-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverHagDisconnect
F77960 | fsmRmtErrComputeBladeDiscover:serialDebugConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to pre-boot environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:serialDebugConnect) | warning | serial-debug-connect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSerialDebugConnect
F77960 | fsmRmtErrComputeBladeDiscover:serialDebugDisconnect | [FSM:STAGE:REMOTE-ERROR]: Disconnect pre-boot environment agent for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiscover:serialDebugDisconnect) | warning | serial-debug-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77960 | fsmRmtErrComputeBladeDiscoverSerialDebugDisconnect
F77960 | fsmRmtErrComputeRackUnitDiscover:BiosPostCompletion | [FSM:STAGE:REMOTE-ERROR]: Waiting for BIOS POST completion from CIMC on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BiosPostCompletion) | warning | bios-post-completion-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBiosPostCompletion
F77960 | fsmRmtErrComputeRackUnitDiscover:BmcConfigPnuOS | [FSM:STAGE:REMOTE-ERROR]: provisioning a bootable device with a bootable pre-boot image for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcConfigPnuOS) | warning | bmc-config-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBmcConfigPnuOS
F77960 | fsmRmtErrComputeRackUnitDiscover:BmcConfigureConnLocal | [FSM:STAGE:REMOTE-ERROR]: Configuring connectivity on CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcConfigureConnLocal) | warning | bmc-configure-conn-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBmcConfigureConnLocal
F77960 | fsmRmtErrComputeRackUnitDiscover:BmcConfigureConnPeer | [FSM:STAGE:REMOTE-ERROR]: Configuring connectivity on CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcConfigureConnPeer) | warning | bmc-configure-conn-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBmcConfigureConnPeer
F77960 | fsmRmtErrComputeRackUnitDiscover:BmcInventory | [FSM:STAGE:REMOTE-ERROR]: getting inventory of server [id] via CIMC(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcInventory) | warning | bmc-inventory-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBmcInventory
F77960 | fsmRmtErrComputeRackUnitDiscover:BmcPreconfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcPreconfigPnuOSLocal) | warning | bmc-preconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBmcPreconfigPnuOSLocal
F77960 | fsmRmtErrComputeRackUnitDiscover:BmcPreconfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcPreconfigPnuOSPeer) | warning | bmc-preconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBmcPreconfigPnuOSPeer
F77960 | fsmRmtErrComputeRackUnitDiscover:BmcPresence | [FSM:STAGE:REMOTE-ERROR]: checking CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcPresence) | warning | bmc-presence-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBmcPresence
F77960 | fsmRmtErrComputeRackUnitDiscover:BmcShutdownDiscovered | [FSM:STAGE:REMOTE-ERROR]: Shutdown the server [id]; deep discovery completed(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcShutdownDiscovered) | warning | bmc-shutdown-discovered-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBmcShutdownDiscovered
F77960 | fsmRmtErrComputeRackUnitDiscover:BmcUnconfigPnuOS | [FSM:STAGE:REMOTE-ERROR]: unprovisioning the bootable device for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BmcUnconfigPnuOS) | warning | bmc-unconfig-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBmcUnconfigPnuOS
F77960 | fsmRmtErrComputeRackUnitDiscover:BootPnuos | [FSM:STAGE:REMOTE-ERROR]: power server [id] on with pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BootPnuos) | warning | boot-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBootPnuos
F77960 | fsmRmtErrComputeRackUnitDiscover:BootWait | [FSM:STAGE:REMOTE-ERROR]: Waiting for system reset on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:BootWait) | warning | boot-wait-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverBootWait
F77960 | fsmRmtErrComputeRackUnitDiscover:ConfigDiscoveryMode | [FSM:STAGE:REMOTE-ERROR]: setting adapter mode to discovery for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:ConfigDiscoveryMode) | warning | config-discovery-mode-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverConfigDiscoveryMode
F77960 | fsmRmtErrComputeRackUnitDiscover:ConfigNivMode | [FSM:STAGE:REMOTE-ERROR]: setting adapter mode to NIV for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:ConfigNivMode) | warning | config-niv-mode-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverConfigNivMode
F77960 | fsmRmtErrComputeRackUnitDiscover:ConfigUserAccess | [FSM:STAGE:REMOTE-ERROR]: configuring external user access to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:ConfigUserAccess) | warning | config-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverConfigUserAccess
F77960 | fsmRmtErrComputeRackUnitDiscover:HandlePooling | [FSM:STAGE:REMOTE-ERROR]: Invoke post-discovery policies on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:HandlePooling) | warning | handle-pooling-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverHandlePooling
F77960 | fsmRmtErrComputeRackUnitDiscover:NicInventoryLocal | [FSM:STAGE:REMOTE-ERROR]: detect and get mezz cards information from [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:NicInventoryLocal) | warning | nic-inventory-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverNicInventoryLocal
F77960 | fsmRmtErrComputeRackUnitDiscover:NicInventoryPeer | [FSM:STAGE:REMOTE-ERROR]: detect and get mezz cards information from [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:NicInventoryPeer) | warning | nic-inventory-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverNicInventoryPeer
F77960 | fsmRmtErrComputeRackUnitDiscover:PnuOSCatalog | [FSM:STAGE:REMOTE-ERROR]: Populate pre-boot catalog to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSCatalog) | warning | pnuoscatalog-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverPnuOSCatalog
F77960 | fsmRmtErrComputeRackUnitDiscover:PnuOSConnStatus | [FSM:STAGE:REMOTE-ERROR]: Explore connectivity of server [id] in pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSConnStatus) | warning | pnuosconn-status-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverPnuOSConnStatus
F77960 | fsmRmtErrComputeRackUnitDiscover:PnuOSConnectivity | [FSM:STAGE:REMOTE-ERROR]: Explore connectivity of server [id] in pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSConnectivity) | warning | pnuosconnectivity-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverPnuOSConnectivity
F77960 | fsmRmtErrComputeRackUnitDiscover:PnuOSIdent | [FSM:STAGE:REMOTE-ERROR]: Identify pre-boot environment agent on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSIdent) | warning | pnuosident-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverPnuOSIdent
F77960 | fsmRmtErrComputeRackUnitDiscover:PnuOSInventory | [FSM:STAGE:REMOTE-ERROR]: Perform inventory of server [id] pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSInventory) | warning | pnuosinventory-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverPnuOSInventory
F77960 | fsmRmtErrComputeRackUnitDiscover:PnuOSPolicy | [FSM:STAGE:REMOTE-ERROR]: Populate pre-boot environment behavior policy to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSPolicy) | warning | pnuospolicy-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverPnuOSPolicy
F77960 | fsmRmtErrComputeRackUnitDiscover:PnuOSScrub | [FSM:STAGE:REMOTE-ERROR]: Scrub server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSScrub) | warning | pnuosscrub-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverPnuOSScrub
F77960 | fsmRmtErrComputeRackUnitDiscover:PnuOSSelfTest | [FSM:STAGE:REMOTE-ERROR]: Trigger self-test of server [id] pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PnuOSSelfTest) | warning | pnuosself-test-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverPnuOSSelfTest
F77960 | fsmRmtErrComputeRackUnitDiscover:PreSanitize | [FSM:STAGE:REMOTE-ERROR]: Preparing to check hardware configuration server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverPreSanitize
F77960 | fsmRmtErrComputeRackUnitDiscover:ReadSmbios | [FSM:STAGE:REMOTE-ERROR]: Waiting for SMBIOS table from CIMC on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:ReadSmbios) | warning | read-smbios-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverReadSmbios
F77960 | fsmRmtErrComputeRackUnitDiscover:Sanitize | [FSM:STAGE:REMOTE-ERROR]: Checking hardware configuration server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSanitize
F77960 | fsmRmtErrComputeRackUnitDiscover:SolRedirectDisable | [FSM:STAGE:REMOTE-ERROR]: Disable Sol Redirection on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SolRedirectDisable) | warning | sol-redirect-disable-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSolRedirectDisable
F77960 | fsmRmtErrComputeRackUnitDiscover:SolRedirectEnable | [FSM:STAGE:REMOTE-ERROR]: set up bios token on server [id] for Sol redirect(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SolRedirectEnable) | warning | sol-redirect-enable-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSolRedirectEnable
F77960 | fsmRmtErrComputeRackUnitDiscover:SwConfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: configure primary fabric interconnect for pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigPnuOSLocal) | warning | sw-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSwConfigPnuOSLocal
F77960 | fsmRmtErrComputeRackUnitDiscover:SwConfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: configure secondary fabric interconnect for pre-boot environment(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigPnuOSPeer) | warning | sw-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSwConfigPnuOSPeer
F77960 | fsmRmtErrComputeRackUnitDiscover:SwConfigPortNivLocal | [FSM:STAGE:REMOTE-ERROR]: configuring primary fabric interconnect access to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigPortNivLocal) | warning | sw-config-port-niv-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSwConfigPortNivLocal
F77960 | fsmRmtErrComputeRackUnitDiscover:SwConfigPortNivPeer | [FSM:STAGE:REMOTE-ERROR]: configuring secondary fabric interconnect access to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigPortNivPeer) | warning | sw-config-port-niv-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSwConfigPortNivPeer
F77960 | fsmRmtErrComputeRackUnitDiscover:SwConfigureConnLocal | [FSM:STAGE:REMOTE-ERROR]: Configuring fabric-interconnect connectivity to CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigureConnLocal) | warning | sw-configure-conn-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSwConfigureConnLocal
F77960 | fsmRmtErrComputeRackUnitDiscover:SwConfigureConnPeer | [FSM:STAGE:REMOTE-ERROR]: Configuring fabric-interconnect connectivity to CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwConfigureConnPeer) | warning | sw-configure-conn-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSwConfigureConnPeer
F77960 | fsmRmtErrComputeRackUnitDiscover:SwPnuOSConnectivityLocal | [FSM:STAGE:REMOTE-ERROR]: determine connectivity of server [id] to fabric(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwPnuOSConnectivityLocal) | warning | sw-pnuosconnectivity-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSwPnuOSConnectivityLocal
F77960 | fsmRmtErrComputeRackUnitDiscover:SwPnuOSConnectivityPeer | [FSM:STAGE:REMOTE-ERROR]: determine connectivity of server [id] to fabric(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwPnuOSConnectivityPeer) | warning | sw-pnuosconnectivity-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSwPnuOSConnectivityPeer
F77960 | fsmRmtErrComputeRackUnitDiscover:SwUnconfigPortNivLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfiguring primary fabric interconnect access to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwUnconfigPortNivLocal) | warning | sw-unconfig-port-niv-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSwUnconfigPortNivLocal
F77960 | fsmRmtErrComputeRackUnitDiscover:SwUnconfigPortNivPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfiguring secondary fabric interconnect access to server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:SwUnconfigPortNivPeer) | warning | sw-unconfig-port-niv-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSwUnconfigPortNivPeer
F77960 | fsmRmtErrComputeRackUnitDiscover:hagConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to pre-boot environment agent on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:hagConnect) | warning | hag-connect-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverHagConnect
F77960 | fsmRmtErrComputeRackUnitDiscover:hagDisconnect | [FSM:STAGE:REMOTE-ERROR]: Disconnect pre-boot environment agent for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:hagDisconnect) | warning | hag-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverHagDisconnect
F77960 | fsmRmtErrComputeRackUnitDiscover:serialDebugConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to pre-boot environment agent on server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:serialDebugConnect) | warning | serial-debug-connect-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSerialDebugConnect
F77960 | fsmRmtErrComputeRackUnitDiscover:serialDebugDisconnect | [FSM:STAGE:REMOTE-ERROR]: Disconnect pre-boot environment agent for server [id](FSM-STAGE:sam:dme:ComputeRackUnitDiscover:serialDebugDisconnect) | warning | serial-debug-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverSerialDebugDisconnect
F77960 | fsmRmtErrComputeRackUnitDiscover:waitForConnReady | [FSM:STAGE:REMOTE-ERROR]: wait for connection to be established(FSM-STAGE:sam:dme:ComputeRackUnitDiscover:waitForConnReady) | warning | wait-for-conn-ready-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 77960 | fsmRmtErrComputeRackUnitDiscoverWaitForConnReady
F77973 | fsmRmtErrEquipmentChassisPsuPolicyConfig:Execute | [FSM:STAGE:REMOTE-ERROR]: Deploying Power Management policy changes on chassis [id](FSM-STAGE:sam:dme:EquipmentChassisPsuPolicyConfig:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 77973 | fsmRmtErrEquipmentChassisPsuPolicyConfigExecute
F77974 | fsmRmtErrAdaptorHostFcIfResetFcPersBinding:ExecuteLocal | [FSM:STAGE:REMOTE-ERROR]: Resetting FC persistent bindings on host interface [dn](FSM-STAGE:sam:dme:AdaptorHostFcIfResetFcPersBinding:ExecuteLocal) | warning | execute-local-failed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 77974 | fsmRmtErrAdaptorHostFcIfResetFcPersBindingExecuteLocal
F77974 | fsmRmtErrAdaptorHostFcIfResetFcPersBinding:ExecutePeer | [FSM:STAGE:REMOTE-ERROR]: Resetting FC persistent bindings on host interface [dn](FSM-STAGE:sam:dme:AdaptorHostFcIfResetFcPersBinding:ExecutePeer) | warning | execute-peer-failed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 77974 | fsmRmtErrAdaptorHostFcIfResetFcPersBindingExecutePeer
F77975 | fsmRmtErrComputeBladeDiag:BiosPostCompletion | [FSM:STAGE:REMOTE-ERROR]: Waiting for BIOS POST completion from CIMC on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:BiosPostCompletion) | warning | bios-post-completion-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagBiosPostCompletion
F77975 | fsmRmtErrComputeBladeDiag:BladeBoot | [FSM:STAGE:REMOTE-ERROR]: Power-on server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:BladeBoot) | warning | blade-boot-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagBladeBoot
F77975 | fsmRmtErrComputeBladeDiag:BladeBootWait | [FSM:STAGE:REMOTE-ERROR]: Waiting for system reset on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:BladeBootWait) | warning | blade-boot-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagBladeBootWait
F77975 | fsmRmtErrComputeBladeDiag:BladePowerOn | [FSM:STAGE:REMOTE-ERROR]: Power on server [chassisId]/[slotId] for diagnostics(FSM-STAGE:sam:dme:ComputeBladeDiag:BladePowerOn) | warning | blade-power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagBladePowerOn
F77975 | fsmRmtErrComputeBladeDiag:BladeReadSmbios | [FSM:STAGE:REMOTE-ERROR]: Read SMBIOS tables on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:BladeReadSmbios) | warning | blade-read-smbios-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagBladeReadSmbios
F77975 | fsmRmtErrComputeBladeDiag:BmcConfigPnuOS | [FSM:STAGE:REMOTE-ERROR]: provisioning a bootable device with a bootable pre-boot image for server(FSM-STAGE:sam:dme:ComputeBladeDiag:BmcConfigPnuOS) | warning | bmc-config-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagBmcConfigPnuOS
F77975 | fsmRmtErrComputeBladeDiag:BmcInventory | [FSM:STAGE:REMOTE-ERROR]: Getting inventory of server [chassisId]/[slotId] via CIMC(FSM-STAGE:sam:dme:ComputeBladeDiag:BmcInventory) | warning | bmc-inventory-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagBmcInventory
F77975 | fsmRmtErrComputeBladeDiag:BmcPresence | [FSM:STAGE:REMOTE-ERROR]: Checking CIMC of server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:BmcPresence) | warning | bmc-presence-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagBmcPresence
F77975 | fsmRmtErrComputeBladeDiag:BmcShutdownDiagCompleted | [FSM:STAGE:REMOTE-ERROR]: Shutdown server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:BmcShutdownDiagCompleted) | warning | bmc-shutdown-diag-completed-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagBmcShutdownDiagCompleted
F77975 | fsmRmtErrComputeBladeDiag:CleanupServerConnSwA | [FSM:STAGE:REMOTE-ERROR]: Cleaning up server [chassisId]/[slotId] interface on fabric A(FSM-STAGE:sam:dme:ComputeBladeDiag:CleanupServerConnSwA) | warning | cleanup-server-conn-sw-afailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagCleanupServerConnSwA
F77975 | fsmRmtErrComputeBladeDiag:CleanupServerConnSwB | [FSM:STAGE:REMOTE-ERROR]: Cleaning up server [chassisId]/[slotId] interface on fabric B(FSM-STAGE:sam:dme:ComputeBladeDiag:CleanupServerConnSwB) | warning | cleanup-server-conn-sw-bfailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagCleanupServerConnSwB
F77975 | fsmRmtErrComputeBladeDiag:ConfigFeLocal | [FSM:STAGE:REMOTE-ERROR]: Configuring primary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:ConfigFeLocal) | warning | config-fe-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagConfigFeLocal
F77975 | fsmRmtErrComputeBladeDiag:ConfigFePeer | [FSM:STAGE:REMOTE-ERROR]: Configuring secondary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:ConfigFePeer) | warning | config-fe-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagConfigFePeer
F77975 | fsmRmtErrComputeBladeDiag:ConfigUserAccess | [FSM:STAGE:REMOTE-ERROR]: Configuring external user access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:ConfigUserAccess) | warning | config-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagConfigUserAccess
F77975 | fsmRmtErrComputeBladeDiag:DebugWait | [FSM:STAGE:REMOTE-ERROR]: Waiting for debugging for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:DebugWait) | warning | debug-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagDebugWait
F77975 | fsmRmtErrComputeBladeDiag:DeriveConfig | [FSM:STAGE:REMOTE-ERROR]: Derive diag config for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:DeriveConfig) | warning | derive-config-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagDeriveConfig
F77975 | fsmRmtErrComputeBladeDiag:DisableServerConnSwA | [FSM:STAGE:REMOTE-ERROR]: Disable server [chassisId]/[slotId] interface on fabric A after completion of network traffic tests on fabric A(FSM-STAGE:sam:dme:ComputeBladeDiag:DisableServerConnSwA) | warning | disable-server-conn-sw-afailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagDisableServerConnSwA
F77975 | fsmRmtErrComputeBladeDiag:DisableServerConnSwB | [FSM:STAGE:REMOTE-ERROR]: Disable server [chassisId]/[slotId] connectivity on fabric B in preparation for network traffic tests on fabric A(FSM-STAGE:sam:dme:ComputeBladeDiag:DisableServerConnSwB) | warning | disable-server-conn-sw-bfailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagDisableServerConnSwB
F77975 | fsmRmtErrComputeBladeDiag:EnableServerConnSwA | [FSM:STAGE:REMOTE-ERROR]: Enable server [chassisId]/[slotId] connectivity on fabric A in preparation for network traffic tests on fabric A(FSM-STAGE:sam:dme:ComputeBladeDiag:EnableServerConnSwA) | warning | enable-server-conn-sw-afailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagEnableServerConnSwA
F77975 | fsmRmtErrComputeBladeDiag:EnableServerConnSwB | [FSM:STAGE:REMOTE-ERROR]: Enable server [chassisId]/[slotId] connectivity on fabric B in preparation for network traffic tests on fabric B(FSM-STAGE:sam:dme:ComputeBladeDiag:EnableServerConnSwB) | warning | enable-server-conn-sw-bfailed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagEnableServerConnSwB
F77975 | fsmRmtErrComputeBladeDiag:EvaluateStatus | [FSM:STAGE:REMOTE-ERROR]: Evaluating status; diagnostics completed(FSM-STAGE:sam:dme:ComputeBladeDiag:EvaluateStatus) | warning | evaluate-status-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagEvaluateStatus
F77975 | fsmRmtErrComputeBladeDiag:FabricATrafficTestStatus | [FSM:STAGE:REMOTE-ERROR]: Gather status of network traffic tests on fabric A for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:FabricATrafficTestStatus) | warning | fabricatraffic-test-status-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagFabricATrafficTestStatus
F77975 | fsmRmtErrComputeBladeDiag:FabricBTrafficTestStatus | [FSM:STAGE:REMOTE-ERROR]: Gather status of network tests on fabric B for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:FabricBTrafficTestStatus) | warning | fabricbtraffic-test-status-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagFabricBTrafficTestStatus
F77975 | fsmRmtErrComputeBladeDiag:GenerateLogWait | [FSM:STAGE:REMOTE-ERROR]: Waiting for collection of diagnostic logs from server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:GenerateLogWait) | warning | generate-log-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagGenerateLogWait
F77975 | fsmRmtErrComputeBladeDiag:GenerateReport | [FSM:STAGE:REMOTE-ERROR]: Generating report for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:GenerateReport) | warning | generate-report-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagGenerateReport
F77975 | fsmRmtErrComputeBladeDiag:HostCatalog | [FSM:STAGE:REMOTE-ERROR]: Populate diagnostics catalog to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostCatalog) | warning | host-catalog-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagHostCatalog
F77975 | fsmRmtErrComputeBladeDiag:HostConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to diagnostics environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostConnect) | warning | host-connect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagHostConnect
F77975 | fsmRmtErrComputeBladeDiag:HostDisconnect | [FSM:STAGE:REMOTE-ERROR]: Disconnect diagnostics environment agent for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostDisconnect) | warning | host-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagHostDisconnect
F77975 | fsmRmtErrComputeBladeDiag:HostIdent | [FSM:STAGE:REMOTE-ERROR]: Identify diagnostics environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostIdent) | warning | host-ident-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagHostIdent
F77975 | fsmRmtErrComputeBladeDiag:HostInventory | [FSM:STAGE:REMOTE-ERROR]: Perform inventory of server [chassisId]/[slotId] in diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:HostInventory) | warning | host-inventory-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagHostInventory
F77975 | fsmRmtErrComputeBladeDiag:HostPolicy | [FSM:STAGE:REMOTE-ERROR]: Populate diagnostics environment behavior policy to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostPolicy) | warning | host-policy-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagHostPolicy
F77975 | fsmRmtErrComputeBladeDiag:HostServerDiag | [FSM:STAGE:REMOTE-ERROR]: Trigger diagnostics on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostServerDiag) | warning | host-server-diag-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagHostServerDiag
F77975 | fsmRmtErrComputeBladeDiag:HostServerDiagStatus | [FSM:STAGE:REMOTE-ERROR]: Diagnostics status on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:HostServerDiagStatus) | warning | host-server-diag-status-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagHostServerDiagStatus
F77975 | fsmRmtErrComputeBladeDiag:NicConfigLocal | [FSM:STAGE:REMOTE-ERROR]: Configure adapter in server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:NicConfigLocal) | warning | nic-config-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagNicConfigLocal
F77975 | fsmRmtErrComputeBladeDiag:NicConfigPeer | [FSM:STAGE:REMOTE-ERROR]: Configure adapter in server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:NicConfigPeer) | warning | nic-config-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagNicConfigPeer
F77975 | fsmRmtErrComputeBladeDiag:NicInventoryLocal | [FSM:STAGE:REMOTE-ERROR]: Retrieve adapter inventory in server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:NicInventoryLocal) | warning | nic-inventory-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagNicInventoryLocal
F77975 | fsmRmtErrComputeBladeDiag:NicInventoryPeer | [FSM:STAGE:REMOTE-ERROR]: Retrieve adapter inventory in server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:NicInventoryPeer) | warning | nic-inventory-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagNicInventoryPeer
F77975 | fsmRmtErrComputeBladeDiag:NicPresenceLocal | [FSM:STAGE:REMOTE-ERROR]: Detect adapter in server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:NicPresenceLocal) | warning | nic-presence-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagNicPresenceLocal
F77975 | fsmRmtErrComputeBladeDiag:NicPresencePeer | [FSM:STAGE:REMOTE-ERROR]: Detect adapter in server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:NicPresencePeer) | warning | nic-presence-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagNicPresencePeer
F77975 | fsmRmtErrComputeBladeDiag:NicUnconfigLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfigure adapter of server [chassisId]/[slotId] diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:NicUnconfigLocal) | warning | nic-unconfig-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagNicUnconfigLocal
F77975 | fsmRmtErrComputeBladeDiag:NicUnconfigPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfigure adapter of server [chassisId]/[slotId] diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:NicUnconfigPeer) | warning | nic-unconfig-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagNicUnconfigPeer
F77975 | fsmRmtErrComputeBladeDiag:RemoveConfig | [FSM:STAGE:REMOTE-ERROR]: Derive diag config for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:RemoveConfig) | warning | remove-config-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagRemoveConfig
F77975 | fsmRmtErrComputeBladeDiag:RemoveVMediaLocal | [FSM:STAGE:REMOTE-ERROR]: Remove VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:RemoveVMediaLocal) | warning | removevmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagRemoveVMediaLocal
F77975 | fsmRmtErrComputeBladeDiag:RemoveVMediaPeer | [FSM:STAGE:REMOTE-ERROR]: Remove VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:RemoveVMediaPeer) | warning | removevmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagRemoveVMediaPeer
F77975 | fsmRmtErrComputeBladeDiag:RestoreConfigFeLocal | [FSM:STAGE:REMOTE-ERROR]: Reconfiguring primary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:RestoreConfigFeLocal) | warning | restore-config-fe-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagRestoreConfigFeLocal
F77975 | fsmRmtErrComputeBladeDiag:RestoreConfigFePeer | [FSM:STAGE:REMOTE-ERROR]: Reconfiguring secondary fabric interconnect access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:RestoreConfigFePeer) | warning | restore-config-fe-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagRestoreConfigFePeer
F77975 | fsmRmtErrComputeBladeDiag:SetDiagUser | [FSM:STAGE:REMOTE-ERROR]: Populate diagnostics environment with a user account to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:SetDiagUser) | warning | set-diag-user-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSetDiagUser
F77975 | fsmRmtErrComputeBladeDiag:SetupVMediaLocal | [FSM:STAGE:REMOTE-ERROR]: Setup VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SetupVMediaLocal) | warning | setupvmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSetupVMediaLocal
F77975 | fsmRmtErrComputeBladeDiag:SetupVMediaPeer | [FSM:STAGE:REMOTE-ERROR]: Setup VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SetupVMediaPeer) | warning | setupvmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSetupVMediaPeer
F77975 | fsmRmtErrComputeBladeDiag:SolRedirectDisable | [FSM:STAGE:REMOTE-ERROR]: Disable Sol Redirection on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:SolRedirectDisable) | warning | sol-redirect-disable-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSolRedirectDisable
F77975 | fsmRmtErrComputeBladeDiag:SolRedirectEnable | [FSM:STAGE:REMOTE-ERROR]: set up bios token on server [chassisId]/[slotId] for Sol redirect(FSM-STAGE:sam:dme:ComputeBladeDiag:SolRedirectEnable) | warning | sol-redirect-enable-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSolRedirectEnable
F77975 | fsmRmtErrComputeBladeDiag:StartFabricATrafficTest | [FSM:STAGE:REMOTE-ERROR]: Trigger network traffic tests on fabric A on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:StartFabricATrafficTest) | warning | start-fabricatraffic-test-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagStartFabricATrafficTest
F77975 | fsmRmtErrComputeBladeDiag:StartFabricBTrafficTest | [FSM:STAGE:REMOTE-ERROR]: Trigger network tests on fabric B for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:StartFabricBTrafficTest) | warning | start-fabricbtraffic-test-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagStartFabricBTrafficTest
F77975 | fsmRmtErrComputeBladeDiag:StopVMediaLocal | [FSM:STAGE:REMOTE-ERROR]: Stop VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:StopVMediaLocal) | warning | stopvmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagStopVMediaLocal
F77975 | fsmRmtErrComputeBladeDiag:StopVMediaPeer | [FSM:STAGE:REMOTE-ERROR]: Stop VMedia for server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:StopVMediaPeer) | warning | stopvmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagStopVMediaPeer
F77975 | fsmRmtErrComputeBladeDiag:SwConfigLocal | [FSM:STAGE:REMOTE-ERROR]: Configure primary fabric interconnect in server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SwConfigLocal) | warning | sw-config-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSwConfigLocal
F77975 | fsmRmtErrComputeBladeDiag:SwConfigPeer | [FSM:STAGE:REMOTE-ERROR]: Configure secondary fabric interconnect in server [chassisId]/[slotId] for diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SwConfigPeer) | warning | sw-config-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSwConfigPeer
F77975 | fsmRmtErrComputeBladeDiag:SwUnconfigLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfigure primary fabric interconnect for server [chassisId]/[slotId] in diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SwUnconfigLocal) | warning | sw-unconfig-local-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSwUnconfigLocal
F77975 | fsmRmtErrComputeBladeDiag:SwUnconfigPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfigure secondary fabric interconnect for server [chassisId]/[slotId] in diagnostics environment(FSM-STAGE:sam:dme:ComputeBladeDiag:SwUnconfigPeer) | warning | sw-unconfig-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSwUnconfigPeer
F77975 | fsmRmtErrComputeBladeDiag:UnconfigUserAccess | [FSM:STAGE:REMOTE-ERROR]: Unconfigure external user access to server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:UnconfigUserAccess) | warning | unconfig-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagUnconfigUserAccess
F77975 | fsmRmtErrComputeBladeDiag:serialDebugConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to pre-boot environment agent on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:serialDebugConnect) | warning | serial-debug-connect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSerialDebugConnect
F77975 | fsmRmtErrComputeBladeDiag:serialDebugDisconnect | [FSM:STAGE:REMOTE-ERROR]: Disconnect pre-boot environment agent for server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeDiag:serialDebugDisconnect) | warning | serial-debug-disconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 77975 | fsmRmtErrComputeBladeDiagSerialDebugDisconnect
F77979 | fsmRmtErrFabricLanCloudSwitchMode:SwConfigLocal | [FSM:STAGE:REMOTE-ERROR]: (FSM-STAGE:sam:dme:FabricLanCloudSwitchMode:SwConfigLocal) | warning | sw-config-local-failed | None set. | None set. | none | TRUE | fsm | fabric:LanCloud | fabric/lan | 77979 | fsmRmtErrFabricLanCloudSwitchModeSwConfigLocal
F77979 | fsmRmtErrFabricLanCloudSwitchMode:SwConfigPeer | [FSM:STAGE:REMOTE-ERROR]: Fabric interconnect mode configuration to primary(FSM-STAGE:sam:dme:FabricLanCloudSwitchMode:SwConfigPeer) | warning | sw-config-peer-failed | None set. | None set. | none | TRUE | fsm | fabric:LanCloud | fabric/lan | 77979 | fsmRmtErrFabricLanCloudSwitchModeSwConfigPeer
F77979 | fsmRmtErrFabricSanCloudSwitchMode:SwConfigLocal | [FSM:STAGE:REMOTE-ERROR]: (FSM-STAGE:sam:dme:FabricSanCloudSwitchMode:SwConfigLocal) | warning | sw-config-local-failed | None set. | None set. | none | TRUE | fsm | fabric:SanCloud | fabric/san | 77979 | fsmRmtErrFabricSanCloudSwitchModeSwConfigLocal
F77979 | fsmRmtErrFabricSanCloudSwitchMode:SwConfigPeer | [FSM:STAGE:REMOTE-ERROR]: Fabric interconnect FC mode configuration to primary(FSM-STAGE:sam:dme:FabricSanCloudSwitchMode:SwConfigPeer) | warning | sw-config-peer-failed | None set. | None set. | none | TRUE | fsm | fabric:SanCloud | fabric/san | 77979 | fsmRmtErrFabricSanCloudSwitchModeSwConfigPeer
F78016 | fsmRmtErrCommSvcEpUpdateSvcEp:PropogateEpSettings | [FSM:STAGE:REMOTE-ERROR]: propogate updated settings (eg. timezone)(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpSettings) | warning | propogate-ep-settings-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78016 | fsmRmtErrCommSvcEpUpdateSvcEpPropogateEpSettings
F78016 | fsmRmtErrCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsLocal | [FSM:STAGE:REMOTE-ERROR]: propogate updated timezone settings to management controllers.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsLocal) | warning | propogate-ep-time-zone-settings-local-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78016 | fsmRmtErrCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsLocal
F78016 | fsmRmtErrCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsPeer | [FSM:STAGE:REMOTE-ERROR]: propogate updated timezone settings to management controllers.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsPeer) | warning | propogate-ep-time-zone-settings-peer-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78016 | fsmRmtErrCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsPeer
F78016 | fsmRmtErrCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToAdaptorsLocal | [FSM:STAGE:REMOTE-ERROR]: propogate updated timezone settings to NICs.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToAdaptorsLocal) | warning | propogate-ep-time-zone-settings-to-adaptors-local-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78016 | fsmRmtErrCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsToAdaptorsLocal
F78016 | fsmRmtErrCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToAdaptorsPeer | [FSM:STAGE:REMOTE-ERROR]: propogate updated timezone settings to NICs.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToAdaptorsPeer) | warning | propogate-ep-time-zone-settings-to-adaptors-peer-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78016 | fsmRmtErrCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsToAdaptorsPeer
F78016 | fsmRmtErrCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToFexIomLocal | [FSM:STAGE:REMOTE-ERROR]: propogate updated timezone settings to FEXs and IOMs.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToFexIomLocal) | warning | propogate-ep-time-zone-settings-to-fex-iom-local-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78016 | fsmRmtErrCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsToFexIomLocal
F78016 | fsmRmtErrCommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToFexIomPeer | [FSM:STAGE:REMOTE-ERROR]: propogate updated timezone settings to FEXs and IOMs.(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:PropogateEpTimeZoneSettingsToFexIomPeer) | warning | propogate-ep-time-zone-settings-to-fex-iom-peer-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78016 | fsmRmtErrCommSvcEpUpdateSvcEpPropogateEpTimeZoneSettingsToFexIomPeer
F78016 | fsmRmtErrCommSvcEpUpdateSvcEp:SetEpLocal | [FSM:STAGE:REMOTE-ERROR]: communication service [name] configuration to primary(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:SetEpLocal) | warning | set-ep-local-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78016 | fsmRmtErrCommSvcEpUpdateSvcEpSetEpLocal
F78016 | fsmRmtErrCommSvcEpUpdateSvcEp:SetEpPeer | [FSM:STAGE:REMOTE-ERROR]: communication service [name] configuration to secondary(FSM-STAGE:sam:dme:CommSvcEpUpdateSvcEp:SetEpPeer) | warning | set-ep-peer-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78016 | fsmRmtErrCommSvcEpUpdateSvcEpSetEpPeer
F78017 | fsmRmtErrCommSvcEpRestartWebSvc:local | [FSM:STAGE:REMOTE-ERROR]: restart web services in primary(FSM-STAGE:sam:dme:CommSvcEpRestartWebSvc:local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78017 | fsmRmtErrCommSvcEpRestartWebSvcLocal
F78017 | fsmRmtErrCommSvcEpRestartWebSvc:peer | [FSM:STAGE:REMOTE-ERROR]: restart web services in secondary(FSM-STAGE:sam:dme:CommSvcEpRestartWebSvc:peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 78017 | fsmRmtErrCommSvcEpRestartWebSvcPeer
F78019 | fsmRmtErrAaaEpUpdateEp:SetEpLocal | [FSM:STAGE:REMOTE-ERROR]: external aaa server configuration to primary(FSM-STAGE:sam:dme:AaaEpUpdateEp:SetEpLocal) | warning | set-ep-local-failed | None set. | None set. | none | TRUE | fsm | aaa:Ep | sys/ | 78019 | fsmRmtErrAaaEpUpdateEpSetEpLocal
F78019 | fsmRmtErrAaaEpUpdateEp:SetEpPeer | [FSM:STAGE:REMOTE-ERROR]: external aaa server configuration to secondary(FSM-STAGE:sam:dme:AaaEpUpdateEp:SetEpPeer) | warning | set-ep-peer-failed | None set. | None set. | none | TRUE | fsm | aaa:Ep | sys/ | 78019 | fsmRmtErrAaaEpUpdateEpSetEpPeer
F78019 | fsmRmtErrPkiEpUpdateEp:SetKeyRingLocal | [FSM:STAGE:REMOTE-ERROR]: keyring configuration on primary(FSM-STAGE:sam:dme:PkiEpUpdateEp:SetKeyRingLocal) | warning | set-key-ring-local-failed | None set. | None set. | none | TRUE | fsm | pki:Ep | sys/pki-ext | 78019 | fsmRmtErrPkiEpUpdateEpSetKeyRingLocal
F78019 | fsmRmtErrPkiEpUpdateEp:SetKeyRingPeer | [FSM:STAGE:REMOTE-ERROR]: keyring configuration on secondary(FSM-STAGE:sam:dme:PkiEpUpdateEp:SetKeyRingPeer) | warning | set-key-ring-peer-failed | None set. | None set. | none | TRUE | fsm | pki:Ep | sys/pki-ext | 78019 | fsmRmtErrPkiEpUpdateEpSetKeyRingPeer
F78019 | fsmRmtErrStatsCollectionPolicyUpdateEp:SetEpA | [FSM:STAGE:REMOTE-ERROR]: Update endpoint on fabric interconnect A(FSM-STAGE:sam:dme:StatsCollectionPolicyUpdateEp:SetEpA) | warning | set-ep-afailed | None set. | None set. | none | TRUE | fsm | stats:CollectionPolicy | stats/coll-policy-[name] | 78019 | fsmRmtErrStatsCollectionPolicyUpdateEpSetEpA
F78019 | fsmRmtErrStatsCollectionPolicyUpdateEp:SetEpB | [FSM:STAGE:REMOTE-ERROR]: Update endpoint on fabric interconnect B(FSM-STAGE:sam:dme:StatsCollectionPolicyUpdateEp:SetEpB) | warning | set-ep-bfailed | None set. | None set. | none | TRUE | fsm | stats:CollectionPolicy | stats/coll-policy-[name] | 78019 | fsmRmtErrStatsCollectionPolicyUpdateEpSetEpB
F78020 | fsmRmtErrAaaRealmUpdateRealm:SetRealmLocal | [FSM:STAGE:REMOTE-ERROR]: realm configuration to primary(FSM-STAGE:sam:dme:AaaRealmUpdateRealm:SetRealmLocal) | warning | set-realm-local-failed | None set. | None set. | none | TRUE | fsm | aaa:Realm | sys/ | 78020 | fsmRmtErrAaaRealmUpdateRealmSetRealmLocal
F78020 | fsmRmtErrAaaRealmUpdateRealm:SetRealmPeer | [FSM:STAGE:REMOTE-ERROR]: realm configuration to secondary(FSM-STAGE:sam:dme:AaaRealmUpdateRealm:SetRealmPeer) | warning | set-realm-peer-failed | None set. | None set. | none | TRUE | fsm | aaa:Realm | sys/ | 78020 | fsmRmtErrAaaRealmUpdateRealmSetRealmPeer
F78021 | fsmRmtErrAaaUserEpUpdateUserEp:SetUserLocal | [FSM:STAGE:REMOTE-ERROR]: user configuration to primary(FSM-STAGE:sam:dme:AaaUserEpUpdateUserEp:SetUserLocal) | warning | set-user-local-failed | None set. | None set. | none | TRUE | fsm | aaa:UserEp | sys/user-ext | 78021 | fsmRmtErrAaaUserEpUpdateUserEpSetUserLocal
F78021 | fsmRmtErrAaaUserEpUpdateUserEp:SetUserPeer | [FSM:STAGE:REMOTE-ERROR]: user configuration to secondary(FSM-STAGE:sam:dme:AaaUserEpUpdateUserEp:SetUserPeer) | warning | set-user-peer-failed | None set. | None set. | none | TRUE | fsm | aaa:UserEp | sys/user-ext | 78021 | fsmRmtErrAaaUserEpUpdateUserEpSetUserPeer
F78040 | fsmRmtErrSysfileMutationSingle:Execute | [FSM:STAGE:REMOTE-ERROR]: [action] file [name](FSM-STAGE:sam:dme:SysfileMutationSingle:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | sysfile:Mutation | sys/corefiles/file-[name]¦[switchId]/mutation | 78040 | fsmRmtErrSysfileMutationSingleExecute
F78041 | fsmRmtErrSysfileMutationGlobal:Local | [FSM:STAGE:REMOTE-ERROR]: remove files from local(FSM-STAGE:sam:dme:SysfileMutationGlobal:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | sysfile:Mutation | sys/corefiles/file-[name]¦[switchId]/mutation | 78041 | fsmRmtErrSysfileMutationGlobalLocal
F78041 | fsmRmtErrSysfileMutationGlobal:Peer | [FSM:STAGE:REMOTE-ERROR]: remove files from peer(FSM-STAGE:sam:dme:SysfileMutationGlobal:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | sysfile:Mutation | sys/corefiles/file-[name]¦[switchId]/mutation | 78041 | fsmRmtErrSysfileMutationGlobalPeer
F78044 | fsmRmtErrSysdebugManualCoreFileExportTargetExport:Execute | [FSM:STAGE:REMOTE-ERROR]: export core file [name] to [hostname](FSM-STAGE:sam:dme:SysdebugManualCoreFileExportTargetExport:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | sysdebug:ManualCoreFileExportTarget | sys/corefiles/file-[name]¦[switchId]/export-to-[hostname] | 78044 | fsmRmtErrSysdebugManualCoreFileExportTargetExportExecute
F78045 | fsmRmtErrFabricEpMgrConfigure:ApplyConfig | [FSM:STAGE:REMOTE-ERROR]: Apply switch configuration(FSM-STAGE:sam:dme:FabricEpMgrConfigure:ApplyConfig) | warning | apply-config-failed | None set. | None set. | none | TRUE | fsm | fabric:EpMgr | fabric/[id] | 78045 | fsmRmtErrFabricEpMgrConfigureApplyConfig
F78045 | fsmRmtErrFabricEpMgrConfigure:ApplyPhysical | [FSM:STAGE:REMOTE-ERROR]: Applying physical configuration(FSM-STAGE:sam:dme:FabricEpMgrConfigure:ApplyPhysical) | warning | apply-physical-failed | None set. | None set. | none | TRUE | fsm | fabric:EpMgr | fabric/[id] | 78045 | fsmRmtErrFabricEpMgrConfigureApplyPhysical
F78045 | fsmRmtErrFabricEpMgrConfigure:ValidateConfiguration | [FSM:STAGE:REMOTE-ERROR]: Validating logical configuration(FSM-STAGE:sam:dme:FabricEpMgrConfigure:ValidateConfiguration) | warning | validate-configuration-failed | None set. | None set. | none | TRUE | fsm | fabric:EpMgr | fabric/[id] | 78045 | fsmRmtErrFabricEpMgrConfigureValidateConfiguration
F78045 | fsmRmtErrFabricEpMgrConfigure:WaitOnPhys | [FSM:STAGE:REMOTE-ERROR]: Waiting on physical change application(FSM-STAGE:sam:dme:FabricEpMgrConfigure:WaitOnPhys) | warning | wait-on-phys-failed | None set. | None set. | none | TRUE | fsm | fabric:EpMgr | fabric/[id] | 78045 | fsmRmtErrFabricEpMgrConfigureWaitOnPhys
F78045 | fsmRmtErrLsServerConfigure:AnalyzeImpact | [FSM:STAGE:REMOTE-ERROR]: Analyzing changes impact(FSM-STAGE:sam:dme:LsServerConfigure:AnalyzeImpact) | warning | analyze-impact-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 78045 | fsmRmtErrLsServerConfigureAnalyzeImpact
F78045 | fsmRmtErrLsServerConfigure:ApplyConfig | [FSM:STAGE:REMOTE-ERROR]: Applying config to server [pnDn](FSM-STAGE:sam:dme:LsServerConfigure:ApplyConfig) | warning | apply-config-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 78045 | fsmRmtErrLsServerConfigureApplyConfig
F78045 | fsmRmtErrLsServerConfigure:ApplyIdentifiers | [FSM:STAGE:REMOTE-ERROR]: Resolving and applying identifiers(FSM-STAGE:sam:dme:LsServerConfigure:ApplyIdentifiers) | warning | apply-identifiers-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 78045 | fsmRmtErrLsServerConfigureApplyIdentifiers
F78045 | fsmRmtErrLsServerConfigure:ApplyPolicies | [FSM:STAGE:REMOTE-ERROR]: Resolving and applying policies(FSM-STAGE:sam:dme:LsServerConfigure:ApplyPolicies) | warning | apply-policies-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 78045 | fsmRmtErrLsServerConfigureApplyPolicies
F78045 | fsmRmtErrLsServerConfigure:ApplyTemplate | [FSM:STAGE:REMOTE-ERROR]: Applying configuration template [srcTemplName](FSM-STAGE:sam:dme:LsServerConfigure:ApplyTemplate) | warning | apply-template-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 78045 | fsmRmtErrLsServerConfigureApplyTemplate
F78045 | fsmRmtErrLsServerConfigure:EvaluateAssociation | [FSM:STAGE:REMOTE-ERROR]: Evaluate association with server [pnDn](FSM-STAGE:sam:dme:LsServerConfigure:EvaluateAssociation) | warning | evaluate-association-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 78045 | fsmRmtErrLsServerConfigureEvaluateAssociation
F78045 | fsmRmtErrLsServerConfigure:ResolveBootConfig | [FSM:STAGE:REMOTE-ERROR]: Computing binding changes(FSM-STAGE:sam:dme:LsServerConfigure:ResolveBootConfig) | warning | resolve-boot-config-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 78045 | fsmRmtErrLsServerConfigureResolveBootConfig
F78045 | fsmRmtErrLsServerConfigure:WaitForMaintPermission | [FSM:STAGE:REMOTE-ERROR]: Waiting for ack or maint window(FSM-STAGE:sam:dme:LsServerConfigure:WaitForMaintPermission) | warning | wait-for-maint-permission-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 78045 | fsmRmtErrLsServerConfigureWaitForMaintPermission
F78045 | fsmRmtErrLsServerConfigure:WaitForMaintWindow | [FSM:STAGE:REMOTE-ERROR]: Waiting for maintenance window(FSM-STAGE:sam:dme:LsServerConfigure:WaitForMaintWindow) | warning | wait-for-maint-window-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 78045 | fsmRmtErrLsServerConfigureWaitForMaintWindow
F78045 | fsmRmtErrSysdebugAutoCoreFileExportTargetConfigure:Local | [FSM:STAGE:REMOTE-ERROR]: configuring automatic core file export service on local(FSM-STAGE:sam:dme:SysdebugAutoCoreFileExportTargetConfigure:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | sysdebug:AutoCoreFileExportTarget | sys/sysdebug/file-export | 78045 | fsmRmtErrSysdebugAutoCoreFileExportTargetConfigureLocal
F78045 | fsmRmtErrSysdebugAutoCoreFileExportTargetConfigure:Peer | [FSM:STAGE:REMOTE-ERROR]: configuring automatic core file export service on peer(FSM-STAGE:sam:dme:SysdebugAutoCoreFileExportTargetConfigure:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | sysdebug:AutoCoreFileExportTarget | sys/sysdebug/file-export | 78045 | fsmRmtErrSysdebugAutoCoreFileExportTargetConfigurePeer
F78046 | fsmRmtErrSysdebugLogControlEpLogControlPersist:Local | [FSM:STAGE:REMOTE-ERROR]: persisting LogControl on local(FSM-STAGE:sam:dme:SysdebugLogControlEpLogControlPersist:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | sysdebug:LogControlEp | sys/sysdebug/logcontrol | 78046 | fsmRmtErrSysdebugLogControlEpLogControlPersistLocal
F78046 | fsmRmtErrSysdebugLogControlEpLogControlPersist:Peer | [FSM:STAGE:REMOTE-ERROR]: persisting LogControl on peer(FSM-STAGE:sam:dme:SysdebugLogControlEpLogControlPersist:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | sysdebug:LogControlEp | sys/sysdebug/logcontrol | 78046 | fsmRmtErrSysdebugLogControlEpLogControlPersistPeer
F78074 | fsmRmtErrEpqosDefinitionDeploy:Local | [FSM:STAGE:REMOTE-ERROR]: vnic qos policy [name] configuration to primary(FSM-STAGE:sam:dme:EpqosDefinitionDeploy:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | epqos:Definition | org-[name]/ep-qos-[name] | 78074 | fsmRmtErrEpqosDefinitionDeployLocal
F78074 | fsmRmtErrEpqosDefinitionDeploy:Peer | [FSM:STAGE:REMOTE-ERROR]: vnic qos policy [name] configuration to secondary(FSM-STAGE:sam:dme:EpqosDefinitionDeploy:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | epqos:Definition | org-[name]/ep-qos-[name] | 78074 | fsmRmtErrEpqosDefinitionDeployPeer
F78074 | fsmRmtErrSwAccessDomainDeploy:UpdateConnectivity | [FSM:STAGE:REMOTE-ERROR]: internal network configuration on [switchId](FSM-STAGE:sam:dme:SwAccessDomainDeploy:UpdateConnectivity) | warning | update-connectivity-failed | None set. | None set. | none | TRUE | fsm | sw:AccessDomain | sys/switch-[id]/access-eth | 78074 | fsmRmtErrSwAccessDomainDeployUpdateConnectivity
F78074 | fsmRmtErrSwEthLanBorderDeploy:UpdateConnectivity | [FSM:STAGE:REMOTE-ERROR]: Uplink eth port configuration on [switchId](FSM-STAGE:sam:dme:SwEthLanBorderDeploy:UpdateConnectivity) | warning | update-connectivity-failed | None set. | None set. | none | TRUE | fsm | sw:EthLanBorder | sys/switch-[id]/border-eth | 78074 | fsmRmtErrSwEthLanBorderDeployUpdateConnectivity
F78074 | fsmRmtErrSwEthMonDeploy:UpdateEthMon | [FSM:STAGE:REMOTE-ERROR]: Ethernet traffic monitor (SPAN)configuration on [switchId](FSM-STAGE:sam:dme:SwEthMonDeploy:UpdateEthMon) | warning | update-eth-mon-failed | None set. | None set. | none | TRUE | fsm | sw:EthMon | sys/switch-[id]/lanmon-eth/mon-[name] | 78074 | fsmRmtErrSwEthMonDeployUpdateEthMon
F78074 | fsmRmtErrSwFcMonDeploy:UpdateFcMon | [FSM:STAGE:REMOTE-ERROR]: FC traffic monitor (SPAN)configuration on [switchId](FSM-STAGE:sam:dme:SwFcMonDeploy:UpdateFcMon) | warning | update-fc-mon-failed | None set. | None set. | none | TRUE | fsm | sw:FcMon | sys/switch-[id]/sanmon-fc/mon-[name] | 78074 | fsmRmtErrSwFcMonDeployUpdateFcMon
F78074 | fsmRmtErrSwFcSanBorderDeploy:UpdateConnectivity | [FSM:STAGE:REMOTE-ERROR]: Uplink fc port configuration on [switchId](FSM-STAGE:sam:dme:SwFcSanBorderDeploy:UpdateConnectivity) | warning | update-connectivity-failed | None set. | None set. | none | TRUE | fsm | sw:FcSanBorder | sys/switch-[id]/border-fc | 78074 | fsmRmtErrSwFcSanBorderDeployUpdateConnectivity
F78074 | fsmRmtErrSwUtilityDomainDeploy:UpdateConnectivity | [FSM:STAGE:REMOTE-ERROR]: Utility network configuration on [switchId](FSM-STAGE:sam:dme:SwUtilityDomainDeploy:UpdateConnectivity) | warning | update-connectivity-failed | None set. | None set. | none | TRUE | fsm | sw:UtilityDomain | sys/switch-[id]/utility-eth | 78074 | fsmRmtErrSwUtilityDomainDeployUpdateConnectivity
F78074 | fsmRmtErrVnicProfileSetDeploy:Local | [FSM:STAGE:REMOTE-ERROR]: VNIC profile configuration on local fabric(FSM-STAGE:sam:dme:VnicProfileSetDeploy:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | vnic:ProfileSet | fabric/lan/profiles | 78074 | fsmRmtErrVnicProfileSetDeployLocal
F78074 | fsmRmtErrVnicProfileSetDeploy:Peer | [FSM:STAGE:REMOTE-ERROR]: VNIC profile configuration on peer fabric(FSM-STAGE:sam:dme:VnicProfileSetDeploy:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | vnic:ProfileSet | fabric/lan/profiles | 78074 | fsmRmtErrVnicProfileSetDeployPeer
F78081 | fsmRmtErrSyntheticFsObjCreate:createLocal | [FSM:STAGE:REMOTE-ERROR]: create on primary(FSM-STAGE:sam:dme:SyntheticFsObjCreate:createLocal) | warning | create-local-failed | None set. | None set. | none | TRUE | fsm | synthetic:FsObj | sys/file-[name] | 78081 | fsmRmtErrSyntheticFsObjCreateCreateLocal
F78081 | fsmRmtErrSyntheticFsObjCreate:createRemote | [FSM:STAGE:REMOTE-ERROR]: create on secondary(FSM-STAGE:sam:dme:SyntheticFsObjCreate:createRemote) | warning | create-remote-failed | None set. | None set. | none | TRUE | fsm | synthetic:FsObj | sys/file-[name] | 78081 | fsmRmtErrSyntheticFsObjCreateCreateRemote
F78091 | fsmRmtErrFirmwareDistributableDelete:Local | [FSM:STAGE:REMOTE-ERROR]: deleting package [name] from primary(FSM-STAGE:sam:dme:FirmwareDistributableDelete:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | firmware:Distributable | sys/fw-catalogue/distrib-[name] | 78091 | fsmRmtErrFirmwareDistributableDeleteLocal
F78091 | fsmRmtErrFirmwareDistributableDelete:Remote | [FSM:STAGE:REMOTE-ERROR]: deleting package [name] from secondary(FSM-STAGE:sam:dme:FirmwareDistributableDelete:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | firmware:Distributable | sys/fw-catalogue/distrib-[name] | 78091 | fsmRmtErrFirmwareDistributableDeleteRemote
F78091 | fsmRmtErrFirmwareImageDelete:Local | [FSM:STAGE:REMOTE-ERROR]: deleting image file [name] ([invTag]) from primary(FSM-STAGE:sam:dme:FirmwareImageDelete:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | firmware:Image | sys/fw-catalogue/image-[name] | 78091 | fsmRmtErrFirmwareImageDeleteLocal
F78091 | fsmRmtErrFirmwareImageDelete:Remote | [FSM:STAGE:REMOTE-ERROR]: deleting image file [name] ([invTag]) from secondary(FSM-STAGE:sam:dme:FirmwareImageDelete:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | firmware:Image | sys/fw-catalogue/image-[name] | 78091 | fsmRmtErrFirmwareImageDeleteRemote
F78093 | fsmRmtErrMgmtControllerUpdateSwitch:resetLocal | [FSM:STAGE:REMOTE-ERROR]: rebooting local fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:resetLocal) | warning | reset-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78093 | fsmRmtErrMgmtControllerUpdateSwitchResetLocal
F78093 | fsmRmtErrMgmtControllerUpdateSwitch:resetRemote | [FSM:STAGE:REMOTE-ERROR]: rebooting remote fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:resetRemote) | warning | reset-remote-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78093 | fsmRmtErrMgmtControllerUpdateSwitchResetRemote
F78093 | fsmRmtErrMgmtControllerUpdateSwitch:updateLocal | [FSM:STAGE:REMOTE-ERROR]: updating local fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:updateLocal) | warning | update-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78093 | fsmRmtErrMgmtControllerUpdateSwitchUpdateLocal
F78093 | fsmRmtErrMgmtControllerUpdateSwitch:updateRemote | [FSM:STAGE:REMOTE-ERROR]: updating peer fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:updateRemote) | warning | update-remote-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78093 | fsmRmtErrMgmtControllerUpdateSwitchUpdateRemote
F78093 | fsmRmtErrMgmtControllerUpdateSwitch:verifyLocal | [FSM:STAGE:REMOTE-ERROR]: verifying boot variables for local fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:verifyLocal) | warning | verify-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78093 | fsmRmtErrMgmtControllerUpdateSwitchVerifyLocal
F78093 | fsmRmtErrMgmtControllerUpdateSwitch:verifyRemote | [FSM:STAGE:REMOTE-ERROR]: verifying boot variables for remote fabric interconnect(FSM-STAGE:sam:dme:MgmtControllerUpdateSwitch:verifyRemote) | warning | verify-remote-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78093 | fsmRmtErrMgmtControllerUpdateSwitchVerifyRemote
F78094 | fsmRmtErrMgmtControllerUpdateIOM:PollUpdateStatus | [FSM:STAGE:REMOTE-ERROR]: waiting for IOM update(FSM-STAGE:sam:dme:MgmtControllerUpdateIOM:PollUpdateStatus) | warning | poll-update-status-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78094 | fsmRmtErrMgmtControllerUpdateIOMPollUpdateStatus
F78094 | fsmRmtErrMgmtControllerUpdateIOM:UpdateRequest | [FSM:STAGE:REMOTE-ERROR]: sending update request to IOM(FSM-STAGE:sam:dme:MgmtControllerUpdateIOM:UpdateRequest) | warning | update-request-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78094 | fsmRmtErrMgmtControllerUpdateIOMUpdateRequest
F78095 | fsmRmtErrMgmtControllerActivateIOM:Activate | [FSM:STAGE:REMOTE-ERROR]: activating backup image of IOM(FSM-STAGE:sam:dme:MgmtControllerActivateIOM:Activate) | warning | activate-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78095 | fsmRmtErrMgmtControllerActivateIOMActivate
F78095 | fsmRmtErrMgmtControllerActivateIOM:Reset | [FSM:STAGE:REMOTE-ERROR]: Resetting IOM to boot the activated version(FSM-STAGE:sam:dme:MgmtControllerActivateIOM:Reset) | warning | reset-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78095 | fsmRmtErrMgmtControllerActivateIOMReset
F78096 | fsmRmtErrMgmtControllerUpdateBMC:PollUpdateStatus | [FSM:STAGE:REMOTE-ERROR]: waiting for update to complete(FSM-STAGE:sam:dme:MgmtControllerUpdateBMC:PollUpdateStatus) | warning | poll-update-status-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78096 | fsmRmtErrMgmtControllerUpdateBMCPollUpdateStatus
F78096 | fsmRmtErrMgmtControllerUpdateBMC:UpdateRequest | [FSM:STAGE:REMOTE-ERROR]: sending update request to CIMC(FSM-STAGE:sam:dme:MgmtControllerUpdateBMC:UpdateRequest) | warning | update-request-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78096 | fsmRmtErrMgmtControllerUpdateBMCUpdateRequest
F78097 | fsmRmtErrMgmtControllerActivateBMC:Activate | [FSM:STAGE:REMOTE-ERROR]: activating backup image of CIMC(FSM-STAGE:sam:dme:MgmtControllerActivateBMC:Activate) | warning | activate-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78097 | fsmRmtErrMgmtControllerActivateBMCActivate
F78097 | fsmRmtErrMgmtControllerActivateBMC:Reset | [FSM:STAGE:REMOTE-ERROR]: Resetting CIMC to boot the activated version(FSM-STAGE:sam:dme:MgmtControllerActivateBMC:Reset) | warning | reset-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78097 | fsmRmtErrMgmtControllerActivateBMCReset
F78110 | fsmRmtErrCallhomeEpConfigCallhome:SetLocal | [FSM:STAGE:REMOTE-ERROR]: call-home configuration on primary(FSM-STAGE:sam:dme:CallhomeEpConfigCallhome:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | callhome:Ep | call-home | 78110 | fsmRmtErrCallhomeEpConfigCallhomeSetLocal
F78110 | fsmRmtErrCallhomeEpConfigCallhome:SetPeer | [FSM:STAGE:REMOTE-ERROR]: call-home configuration on secondary(FSM-STAGE:sam:dme:CallhomeEpConfigCallhome:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | callhome:Ep | call-home | 78110 | fsmRmtErrCallhomeEpConfigCallhomeSetPeer
F78113 | fsmRmtErrMgmtIfSwMgmtOobIfConfig:Switch | [FSM:STAGE:REMOTE-ERROR]: configuring the out-of-band interface(FSM-STAGE:sam:dme:MgmtIfSwMgmtOobIfConfig:Switch) | warning | switch-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 78113 | fsmRmtErrMgmtIfSwMgmtOobIfConfigSwitch
F78114 | fsmRmtErrMgmtIfSwMgmtInbandIfConfig:Switch | [FSM:STAGE:REMOTE-ERROR]: configuring the inband interface(FSM-STAGE:sam:dme:MgmtIfSwMgmtInbandIfConfig:Switch) | warning | switch-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 78114 | fsmRmtErrMgmtIfSwMgmtInbandIfConfigSwitch
F78119 | fsmRmtErrMgmtIfVirtualIfConfig:Local | [FSM:STAGE:REMOTE-ERROR]: Updating virtual interface on local fabric interconnect(FSM-STAGE:sam:dme:MgmtIfVirtualIfConfig:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 78119 | fsmRmtErrMgmtIfVirtualIfConfigLocal
F78119 | fsmRmtErrMgmtIfVirtualIfConfig:Remote | [FSM:STAGE:REMOTE-ERROR]: Updating virtual interface on peer fabric interconnect(FSM-STAGE:sam:dme:MgmtIfVirtualIfConfig:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 78119 | fsmRmtErrMgmtIfVirtualIfConfigRemote
F78120 | fsmRmtErrMgmtIfEnableVip:Local | [FSM:STAGE:REMOTE-ERROR]: Enable virtual interface on local fabric interconnect(FSM-STAGE:sam:dme:MgmtIfEnableVip:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 78120 | fsmRmtErrMgmtIfEnableVipLocal
F78121 | fsmRmtErrMgmtIfDisableVip:Peer | [FSM:STAGE:REMOTE-ERROR]: Disable virtual interface on peer fabric interconnect(FSM-STAGE:sam:dme:MgmtIfDisableVip:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 78121 | fsmRmtErrMgmtIfDisableVipPeer
F78122 | fsmRmtErrMgmtIfEnableHA:Local | [FSM:STAGE:REMOTE-ERROR]: Transition from single to cluster mode(FSM-STAGE:sam:dme:MgmtIfEnableHA:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 78122 | fsmRmtErrMgmtIfEnableHALocal
F78123 | fsmRmtErrMgmtBackupBackup:backupLocal | [FSM:STAGE:REMOTE-ERROR]: internal database backup(FSM-STAGE:sam:dme:MgmtBackupBackup:backupLocal) | warning | backup-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Backup | sys/backup-[hostname] | 78123 | fsmRmtErrMgmtBackupBackupBackupLocal
F78123 | fsmRmtErrMgmtBackupBackup:upload | [FSM:STAGE:REMOTE-ERROR]: internal system backup(FSM-STAGE:sam:dme:MgmtBackupBackup:upload) | warning | upload-failed | None set. | None set. | none | TRUE | fsm | mgmt:Backup | sys/backup-[hostname] | 78123 | fsmRmtErrMgmtBackupBackupUpload
F78124 | fsmRmtErrMgmtImporterImport:config | [FSM:STAGE:REMOTE-ERROR]: importing the configuration file(FSM-STAGE:sam:dme:MgmtImporterImport:config) | warning | config-failed | None set. | None set. | none | TRUE | fsm | mgmt:Importer | sys/import-config-[hostname] | 78124 | fsmRmtErrMgmtImporterImportConfig
F78124 | fsmRmtErrMgmtImporterImport:downloadLocal | [FSM:STAGE:REMOTE-ERROR]: downloading the configuration file from the remote location(FSM-STAGE:sam:dme:MgmtImporterImport:downloadLocal) | warning | download-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Importer | sys/import-config-[hostname] | 78124 | fsmRmtErrMgmtImporterImportDownloadLocal
F78124 | fsmRmtErrMgmtImporterImport:reportResults | [FSM:STAGE:REMOTE-ERROR]: Report results of configuration application(FSM-STAGE:sam:dme:MgmtImporterImport:reportResults) | warning | report-results-failed | None set. | None set. | none | TRUE | fsm | mgmt:Importer | sys/import-config-[hostname] | 78124 | fsmRmtErrMgmtImporterImportReportResults
F78185 | fsmRmtErrQosclassDefinitionConfigGlobalQoS:SetLocal | [FSM:STAGE:REMOTE-ERROR]: QoS Classification Definition [name] configuration on primary(FSM-STAGE:sam:dme:QosclassDefinitionConfigGlobalQoS:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | qosclass:Definition | fabric/lan/classes | 78185 | fsmRmtErrQosclassDefinitionConfigGlobalQoSSetLocal
F78185 | fsmRmtErrQosclassDefinitionConfigGlobalQoS:SetPeer | [FSM:STAGE:REMOTE-ERROR]: QoS Classification Definition [name] configuration on secondary(FSM-STAGE:sam:dme:QosclassDefinitionConfigGlobalQoS:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | qosclass:Definition | fabric/lan/classes | 78185 | fsmRmtErrQosclassDefinitionConfigGlobalQoSSetPeer
F78190 | fsmRmtErrEpqosDefinitionDelTaskRemove:Local | [FSM:STAGE:REMOTE-ERROR]: vnic qos policy [name] removal from primary(FSM-STAGE:sam:dme:EpqosDefinitionDelTaskRemove:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | epqos:DefinitionDelTask | org-[name]/ep-qos-deletion-[defIntId] | 78190 | fsmRmtErrEpqosDefinitionDelTaskRemoveLocal
F78190 | fsmRmtErrEpqosDefinitionDelTaskRemove:Peer | [FSM:STAGE:REMOTE-ERROR]: vnic qos policy [name] removal from secondary(FSM-STAGE:sam:dme:EpqosDefinitionDelTaskRemove:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | epqos:DefinitionDelTask | org-[name]/ep-qos-deletion-[defIntId] | 78190 | fsmRmtErrEpqosDefinitionDelTaskRemovePeer
F78243 | fsmRmtErrEquipmentIOCardResetCmc:Execute | [FSM:STAGE:REMOTE-ERROR]: Resetting Chassis Management Controller on IOM [chassisId]/[id](FSM-STAGE:sam:dme:EquipmentIOCardResetCmc:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 78243 | fsmRmtErrEquipmentIOCardResetCmcExecute
F78255 | fsmRmtErrMgmtControllerUpdateUCSManager:execute | [FSM:STAGE:REMOTE-ERROR]: Updating UCS Manager firmware(FSM-STAGE:sam:dme:MgmtControllerUpdateUCSManager:execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78255 | fsmRmtErrMgmtControllerUpdateUCSManagerExecute
F78255 | fsmRmtErrMgmtControllerUpdateUCSManager:start | [FSM:STAGE:REMOTE-ERROR]: Scheduling UCS manager update(FSM-STAGE:sam:dme:MgmtControllerUpdateUCSManager:start) | warning | start-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78255 | fsmRmtErrMgmtControllerUpdateUCSManagerStart
F78263 | fsmRmtErrMgmtControllerSysConfig:Primary | [FSM:STAGE:REMOTE-ERROR]: system configuration on primary(FSM-STAGE:sam:dme:MgmtControllerSysConfig:Primary) | warning | primary-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78263 | fsmRmtErrMgmtControllerSysConfigPrimary
F78263 | fsmRmtErrMgmtControllerSysConfig:Secondary | [FSM:STAGE:REMOTE-ERROR]: system configuration on secondary(FSM-STAGE:sam:dme:MgmtControllerSysConfig:Secondary) | warning | secondary-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78263 | fsmRmtErrMgmtControllerSysConfigSecondary
F78292 | fsmRmtErrAdaptorExtEthIfPathReset:Disable | [FSM:STAGE:REMOTE-ERROR]: Disable path [side]([switchId]) on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorExtEthIfPathReset:Disable) | warning | disable-failed | None set. | None set. | none | TRUE | fsm | adaptor:ExtEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/ext-eth-[id] | 78292 | fsmRmtErrAdaptorExtEthIfPathResetDisable
F78292 | fsmRmtErrAdaptorExtEthIfPathReset:Enable | [FSM:STAGE:REMOTE-ERROR]: Enabe path [side]([switchId]) on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorExtEthIfPathReset:Enable) | warning | enable-failed | None set. | None set. | none | TRUE | fsm | adaptor:ExtEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/ext-eth-[id] | 78292 | fsmRmtErrAdaptorExtEthIfPathResetEnable
F78297 | fsmRmtErrAdaptorHostEthIfCircuitReset:DisableA | [FSM:STAGE:REMOTE-ERROR]: Disable circuit A for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostEthIfCircuitReset:DisableA) | warning | disable-afailed | None set. | None set. | none | TRUE | fsm | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 78297 | fsmRmtErrAdaptorHostEthIfCircuitResetDisableA
F78297 | fsmRmtErrAdaptorHostEthIfCircuitReset:DisableB | [FSM:STAGE:REMOTE-ERROR]: Disable circuit B for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostEthIfCircuitReset:DisableB) | warning | disable-bfailed | None set. | None set. | none | TRUE | fsm | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 78297 | fsmRmtErrAdaptorHostEthIfCircuitResetDisableB
F78297 | fsmRmtErrAdaptorHostEthIfCircuitReset:EnableA | [FSM:STAGE:REMOTE-ERROR]: Enable circuit A for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostEthIfCircuitReset:EnableA) | warning | enable-afailed | None set. | None set. | none | TRUE | fsm | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 78297 | fsmRmtErrAdaptorHostEthIfCircuitResetEnableA
F78297 | fsmRmtErrAdaptorHostEthIfCircuitReset:EnableB | [FSM:STAGE:REMOTE-ERROR]: Enable circuit B for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostEthIfCircuitReset:EnableB) | warning | enable-bfailed | None set. | None set. | none | TRUE | fsm | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 78297 | fsmRmtErrAdaptorHostEthIfCircuitResetEnableB
F78297 | fsmRmtErrAdaptorHostFcIfCircuitReset:DisableA | [FSM:STAGE:REMOTE-ERROR]: Disable circuit A for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostFcIfCircuitReset:DisableA) | warning | disable-afailed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 78297 | fsmRmtErrAdaptorHostFcIfCircuitResetDisableA
F78297 | fsmRmtErrAdaptorHostFcIfCircuitReset:DisableB | [FSM:STAGE:REMOTE-ERROR]: Disable circuit B for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostFcIfCircuitReset:DisableB) | warning | disable-bfailed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 78297 | fsmRmtErrAdaptorHostFcIfCircuitResetDisableB
F78297 | fsmRmtErrAdaptorHostFcIfCircuitReset:EnableA | [FSM:STAGE:REMOTE-ERROR]: Enable circuit A for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostFcIfCircuitReset:EnableA) | warning | enable-afailed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 78297 | fsmRmtErrAdaptorHostFcIfCircuitResetEnableA
F78297 | fsmRmtErrAdaptorHostFcIfCircuitReset:EnableB | [FSM:STAGE:REMOTE-ERROR]: Enable circuit B for host adaptor [id] on server [chassisId]/[slotId](FSM-STAGE:sam:dme:AdaptorHostFcIfCircuitReset:EnableB) | warning | enable-bfailed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 78297 | fsmRmtErrAdaptorHostFcIfCircuitResetEnableB
F78319 | fsmRmtErrExtvmmMasterExtKeyConfig:SetLocal | [FSM:STAGE:REMOTE-ERROR]: external VM manager extension-key configuration on peer fabric(FSM-STAGE:sam:dme:ExtvmmMasterExtKeyConfig:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | extvmm:MasterExtKey | sys/extvm-mgmt/ext-key | 78319 | fsmRmtErrExtvmmMasterExtKeyConfigSetLocal
F78319 | fsmRmtErrExtvmmMasterExtKeyConfig:SetPeer | [FSM:STAGE:REMOTE-ERROR]: external VM manager extension-key configuration on local fabric(FSM-STAGE:sam:dme:ExtvmmMasterExtKeyConfig:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | extvmm:MasterExtKey | sys/extvm-mgmt/ext-key | 78319 | fsmRmtErrExtvmmMasterExtKeyConfigSetPeer
F78319 | fsmRmtErrExtvmmProviderConfig:GetVersion | [FSM:STAGE:REMOTE-ERROR]: external VM manager version fetch(FSM-STAGE:sam:dme:ExtvmmProviderConfig:GetVersion) | warning | get-version-failed | None set. | None set. | none | TRUE | fsm | extvmm:Provider | sys/extvm-mgmt/vm-[name] | 78319 | fsmRmtErrExtvmmProviderConfigGetVersion
F78319 | fsmRmtErrExtvmmProviderConfig:SetLocal | [FSM:STAGE:REMOTE-ERROR]: external VM manager configuration on local fabric(FSM-STAGE:sam:dme:ExtvmmProviderConfig:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | extvmm:Provider | sys/extvm-mgmt/vm-[name] | 78319 | fsmRmtErrExtvmmProviderConfigSetLocal
F78319 | fsmRmtErrExtvmmProviderConfig:SetPeer | [FSM:STAGE:REMOTE-ERROR]: external VM manager configuration on peer fabric(FSM-STAGE:sam:dme:ExtvmmProviderConfig:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | extvmm:Provider | sys/extvm-mgmt/vm-[name] | 78319 | fsmRmtErrExtvmmProviderConfigSetPeer
F78319 | fsmRmtErrVmLifeCyclePolicyConfig:Local | [FSM:STAGE:REMOTE-ERROR]: set Veth Auto-delete Retention Timer on local fabric(FSM-STAGE:sam:dme:VmLifeCyclePolicyConfig:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | vm:LifeCyclePolicy | org-[name]/vm-lc-policy | 78319 | fsmRmtErrVmLifeCyclePolicyConfigLocal
F78319 | fsmRmtErrVmLifeCyclePolicyConfig:Peer | [FSM:STAGE:REMOTE-ERROR]: set Veth Auto-delete Retention Timer on peer fabric(FSM-STAGE:sam:dme:VmLifeCyclePolicyConfig:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | vm:LifeCyclePolicy | org-[name]/vm-lc-policy | 78319 | fsmRmtErrVmLifeCyclePolicyConfigPeer
F78320 | fsmRmtErrExtvmmKeyStoreCertInstall:SetLocal | [FSM:STAGE:REMOTE-ERROR]: external VM manager cetificate configuration on local fabric(FSM-STAGE:sam:dme:ExtvmmKeyStoreCertInstall:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | extvmm:KeyStore | sys/extvm-mgmt/key-store | 78320 | fsmRmtErrExtvmmKeyStoreCertInstallSetLocal
F78320 | fsmRmtErrExtvmmKeyStoreCertInstall:SetPeer | [FSM:STAGE:REMOTE-ERROR]: external VM manager certificate configuration on peer fabric(FSM-STAGE:sam:dme:ExtvmmKeyStoreCertInstall:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | extvmm:KeyStore | sys/extvm-mgmt/key-store | 78320 | fsmRmtErrExtvmmKeyStoreCertInstallSetPeer
F78321 | fsmRmtErrExtvmmSwitchDelTaskRemoveProvider:RemoveLocal | [FSM:STAGE:REMOTE-ERROR]: external VM manager deletion from local fabric(FSM-STAGE:sam:dme:ExtvmmSwitchDelTaskRemoveProvider:RemoveLocal) | warning | remove-local-failed | None set. | None set. | none | TRUE | fsm | extvmm:SwitchDelTask | sys/extvm-mgmt/vsw-deltask-[swIntId] | 78321 | fsmRmtErrExtvmmSwitchDelTaskRemoveProviderRemoveLocal
F78344 | fsmRmtErrCapabilityUpdaterUpdater:Apply | [FSM:STAGE:REMOTE-ERROR]: applying changes to catalog(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:Apply) | warning | apply-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 78344 | fsmRmtErrCapabilityUpdaterUpdaterApply
F78344 | fsmRmtErrCapabilityUpdaterUpdater:CopyRemote | [FSM:STAGE:REMOTE-ERROR]: syncing catalog files to subordinate(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:CopyRemote) | warning | copy-remote-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 78344 | fsmRmtErrCapabilityUpdaterUpdaterCopyRemote
F78344 | fsmRmtErrCapabilityUpdaterUpdater:DeleteLocal | [FSM:STAGE:REMOTE-ERROR]: deleting temp image [fileName] on local(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:DeleteLocal) | warning | delete-local-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 78344 | fsmRmtErrCapabilityUpdaterUpdaterDeleteLocal
F78344 | fsmRmtErrCapabilityUpdaterUpdater:EvaluateStatus | [FSM:STAGE:REMOTE-ERROR]: evaluating status of update(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:EvaluateStatus) | warning | evaluate-status-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 78344 | fsmRmtErrCapabilityUpdaterUpdaterEvaluateStatus
F78344 | fsmRmtErrCapabilityUpdaterUpdater:Local | [FSM:STAGE:REMOTE-ERROR]: downloading catalog file [fileName] from [server](FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 78344 | fsmRmtErrCapabilityUpdaterUpdaterLocal
F78344 | fsmRmtErrCapabilityUpdaterUpdater:RescanImages | [FSM:STAGE:REMOTE-ERROR]: rescanning image files(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:RescanImages) | warning | rescan-images-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 78344 | fsmRmtErrCapabilityUpdaterUpdaterRescanImages
F78344 | fsmRmtErrCapabilityUpdaterUpdater:UnpackLocal | [FSM:STAGE:REMOTE-ERROR]: unpacking catalog file [fileName] on primary(FSM-STAGE:sam:dme:CapabilityUpdaterUpdater:UnpackLocal) | warning | unpack-local-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 78344 | fsmRmtErrCapabilityUpdaterUpdaterUnpackLocal
F78370 | fsmRmtErrComputeBladeUpdateBoardController:BladePowerOff | [FSM:STAGE:REMOTE-ERROR]: Power off server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeUpdateBoardController:BladePowerOff) | warning | blade-power-off-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 78370 | fsmRmtErrComputeBladeUpdateBoardControllerBladePowerOff
F78370 | fsmRmtErrComputeBladeUpdateBoardController:BladePowerOn | [FSM:STAGE:REMOTE-ERROR]: Power on server [chassisId]/[slotId](FSM-STAGE:sam:dme:ComputeBladeUpdateBoardController:BladePowerOn) | warning | blade-power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 78370 | fsmRmtErrComputeBladeUpdateBoardControllerBladePowerOn
F78370 | fsmRmtErrComputeBladeUpdateBoardController:PollUpdateStatus | [FSM:STAGE:REMOTE-ERROR]: Waiting for Board Controller update to complete(FSM-STAGE:sam:dme:ComputeBladeUpdateBoardController:PollUpdateStatus) | warning | poll-update-status-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 78370 | fsmRmtErrComputeBladeUpdateBoardControllerPollUpdateStatus
F78370 | fsmRmtErrComputeBladeUpdateBoardController:PrepareForUpdate | [FSM:STAGE:REMOTE-ERROR]: Prepare for BoardController update(FSM-STAGE:sam:dme:ComputeBladeUpdateBoardController:PrepareForUpdate) | warning | prepare-for-update-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 78370 | fsmRmtErrComputeBladeUpdateBoardControllerPrepareForUpdate
F78370 | fsmRmtErrComputeBladeUpdateBoardController:UpdateRequest | [FSM:STAGE:REMOTE-ERROR]: Sending Board Controller update request to CIMC(FSM-STAGE:sam:dme:ComputeBladeUpdateBoardController:UpdateRequest) | warning | update-request-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 78370 | fsmRmtErrComputeBladeUpdateBoardControllerUpdateRequest
F78371 | fsmRmtErrCapabilityCatalogueDeployCatalogue:SyncBladeAGLocal | [FSM:STAGE:REMOTE-ERROR]: Sending capability catalogue [version] to local bladeAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncBladeAGLocal) | warning | sync-bladeaglocal-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78371 | fsmRmtErrCapabilityCatalogueDeployCatalogueSyncBladeAGLocal
F78371 | fsmRmtErrCapabilityCatalogueDeployCatalogue:SyncBladeAGRemote | [FSM:STAGE:REMOTE-ERROR]: Sending capability catalogue [version] to remote bladeAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncBladeAGRemote) | warning | sync-bladeagremote-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78371 | fsmRmtErrCapabilityCatalogueDeployCatalogueSyncBladeAGRemote
F78371 | fsmRmtErrCapabilityCatalogueDeployCatalogue:SyncHostagentAGLocal | [FSM:STAGE:REMOTE-ERROR]: Sending capability catalogue [version] to local hostagentAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncHostagentAGLocal) | warning | sync-hostagentaglocal-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78371 | fsmRmtErrCapabilityCatalogueDeployCatalogueSyncHostagentAGLocal
F78371 | fsmRmtErrCapabilityCatalogueDeployCatalogue:SyncHostagentAGRemote | [FSM:STAGE:REMOTE-ERROR]: Sending capability catalogue [version] to remote hostagentAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncHostagentAGRemote) | warning | sync-hostagentagremote-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78371 | fsmRmtErrCapabilityCatalogueDeployCatalogueSyncHostagentAGRemote
F78371 | fsmRmtErrCapabilityCatalogueDeployCatalogue:SyncNicAGLocal | [FSM:STAGE:REMOTE-ERROR]: Sending capability catalogue [version] to local nicAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncNicAGLocal) | warning | sync-nicaglocal-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78371 | fsmRmtErrCapabilityCatalogueDeployCatalogueSyncNicAGLocal
F78371 | fsmRmtErrCapabilityCatalogueDeployCatalogue:SyncNicAGRemote | [FSM:STAGE:REMOTE-ERROR]: Sending capability catalogue [version] to remote nicAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncNicAGRemote) | warning | sync-nicagremote-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78371 | fsmRmtErrCapabilityCatalogueDeployCatalogueSyncNicAGRemote
F78371 | fsmRmtErrCapabilityCatalogueDeployCatalogue:SyncPortAGLocal | [FSM:STAGE:REMOTE-ERROR]: Sending capability catalogue [version] to local portAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncPortAGLocal) | warning | sync-portaglocal-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78371 | fsmRmtErrCapabilityCatalogueDeployCatalogueSyncPortAGLocal
F78371 | fsmRmtErrCapabilityCatalogueDeployCatalogue:SyncPortAGRemote | [FSM:STAGE:REMOTE-ERROR]: Sending capability catalogue [version] to remote portAG(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:SyncPortAGRemote) | warning | sync-portagremote-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78371 | fsmRmtErrCapabilityCatalogueDeployCatalogueSyncPortAGRemote
F78371 | fsmRmtErrCapabilityCatalogueDeployCatalogue:finalize | [FSM:STAGE:REMOTE-ERROR]: Finalizing capability catalogue [version] deployment(FSM-STAGE:sam:dme:CapabilityCatalogueDeployCatalogue:finalize) | warning | finalize-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78371 | fsmRmtErrCapabilityCatalogueDeployCatalogueFinalize
F78382 | fsmRmtErrEquipmentFexRemoveFex:CleanupEntries | [FSM:STAGE:REMOTE-ERROR]: cleaning host entries(FSM-STAGE:sam:dme:EquipmentFexRemoveFex:CleanupEntries) | warning | cleanup-entries-failed | None set. | None set. | none | TRUE | fsm | equipment:Fex | sys/fex-[id] | 78382 | fsmRmtErrEquipmentFexRemoveFexCleanupEntries
F78382 | fsmRmtErrEquipmentFexRemoveFex:UnIdentifyLocal | [FSM:STAGE:REMOTE-ERROR]: erasing fex identity [id] from primary(FSM-STAGE:sam:dme:EquipmentFexRemoveFex:UnIdentifyLocal) | warning | un-identify-local-failed | None set. | None set. | none | TRUE | fsm | equipment:Fex | sys/fex-[id] | 78382 | fsmRmtErrEquipmentFexRemoveFexUnIdentifyLocal
F78382 | fsmRmtErrEquipmentFexRemoveFex:Wait | [FSM:STAGE:REMOTE-ERROR]: waiting for clean up of resources for chassis [id] (approx. 2 min)(FSM-STAGE:sam:dme:EquipmentFexRemoveFex:Wait) | warning | wait-failed | None set. | None set. | none | TRUE | fsm | equipment:Fex | sys/fex-[id] | 78382 | fsmRmtErrEquipmentFexRemoveFexWait
F78382 | fsmRmtErrEquipmentFexRemoveFex:decomission | [FSM:STAGE:REMOTE-ERROR]: decomissioning fex [id](FSM-STAGE:sam:dme:EquipmentFexRemoveFex:decomission) | warning | decomission-failed | None set. | None set. | none | TRUE | fsm | equipment:Fex | sys/fex-[id] | 78382 | fsmRmtErrEquipmentFexRemoveFexDecomission
F78383 | fsmRmtErrEquipmentLocatorLedSetFeLocatorLed:Execute | [FSM:STAGE:REMOTE-ERROR]: setting locator led to [adminState](FSM-STAGE:sam:dme:EquipmentLocatorLedSetFeLocatorLed:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:LocatorLed | sys/chassis-[id]/blade-[slotId]/locator-led | 78383 | fsmRmtErrEquipmentLocatorLedSetFeLocatorLedExecute
F78384 | fsmRmtErrComputePhysicalPowerCap:Config | [FSM:STAGE:REMOTE-ERROR]: Configuring power cap of server [dn](FSM-STAGE:sam:dme:ComputePhysicalPowerCap:Config) | warning | config-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78384 | fsmRmtErrComputePhysicalPowerCapConfig
F78384 | fsmRmtErrEquipmentChassisPowerCap:Config | [FSM:STAGE:REMOTE-ERROR]: (FSM-STAGE:sam:dme:EquipmentChassisPowerCap:Config) | warning | config-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 78384 | fsmRmtErrEquipmentChassisPowerCapConfig
F78385 | fsmRmtErrEquipmentIOCardMuxOffline:CleanupEntries | [FSM:STAGE:REMOTE-ERROR]: cleaning host entries(FSM-STAGE:sam:dme:EquipmentIOCardMuxOffline:CleanupEntries) | warning | cleanup-entries-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 78385 | fsmRmtErrEquipmentIOCardMuxOfflineCleanupEntries
F78413 | fsmRmtErrComputePhysicalAssociate:ActivateBios | [FSM:STAGE:REMOTE-ERROR]: Activate BIOS image for server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:ActivateBios) | warning | activate-bios-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateActivateBios
F78413 | fsmRmtErrComputePhysicalAssociate:BiosImgUpdate | [FSM:STAGE:REMOTE-ERROR]: Update blade BIOS image(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BiosImgUpdate) | warning | bios-img-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateBiosImgUpdate
F78413 | fsmRmtErrComputePhysicalAssociate:BiosPostCompletion | [FSM:STAGE:REMOTE-ERROR]: Waiting for BIOS POST completion from CIMC on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:BiosPostCompletion) | warning | bios-post-completion-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateBiosPostCompletion
F78413 | fsmRmtErrComputePhysicalAssociate:BladePowerOff | [FSM:STAGE:REMOTE-ERROR]: Power off server for configuration of service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:BladePowerOff) | warning | blade-power-off-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateBladePowerOff
F78413 | fsmRmtErrComputePhysicalAssociate:BmcConfigPnuOS | [FSM:STAGE:REMOTE-ERROR]: provisioning a bootable device with a bootable pre-boot image for server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BmcConfigPnuOS) | warning | bmc-config-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateBmcConfigPnuOS
F78413 | fsmRmtErrComputePhysicalAssociate:BmcPreconfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BmcPreconfigPnuOSLocal) | warning | bmc-preconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateBmcPreconfigPnuOSLocal
F78413 | fsmRmtErrComputePhysicalAssociate:BmcPreconfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BmcPreconfigPnuOSPeer) | warning | bmc-preconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateBmcPreconfigPnuOSPeer
F78413 | fsmRmtErrComputePhysicalAssociate:BmcUnconfigPnuOS | [FSM:STAGE:REMOTE-ERROR]: unprovisioning the bootable device for server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BmcUnconfigPnuOS) | warning | bmc-unconfig-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateBmcUnconfigPnuOS
F78413 | fsmRmtErrComputePhysicalAssociate:BootHost | [FSM:STAGE:REMOTE-ERROR]: Boot host OS for server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BootHost) | warning | boot-host-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateBootHost
F78413 | fsmRmtErrComputePhysicalAssociate:BootPnuos | [FSM:STAGE:REMOTE-ERROR]: Bring-up pre-boot environment for association with [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:BootPnuos) | warning | boot-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateBootPnuos
F78413 | fsmRmtErrComputePhysicalAssociate:BootWait | [FSM:STAGE:REMOTE-ERROR]: Waiting for system reset(FSM-STAGE:sam:dme:ComputePhysicalAssociate:BootWait) | warning | boot-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateBootWait
F78413 | fsmRmtErrComputePhysicalAssociate:ClearBiosUpdate | [FSM:STAGE:REMOTE-ERROR]: Clearing pending BIOS image update(FSM-STAGE:sam:dme:ComputePhysicalAssociate:ClearBiosUpdate) | warning | clear-bios-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateClearBiosUpdate
F78413 | fsmRmtErrComputePhysicalAssociate:ConfigSoL | [FSM:STAGE:REMOTE-ERROR]: Configuring SoL interface on server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:ConfigSoL) | warning | config-so-lfailed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateConfigSoL
F78413 | fsmRmtErrComputePhysicalAssociate:ConfigUserAccess | [FSM:STAGE:REMOTE-ERROR]: Configuring external user access(FSM-STAGE:sam:dme:ComputePhysicalAssociate:ConfigUserAccess) | warning | config-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateConfigUserAccess
F78413 | fsmRmtErrComputePhysicalAssociate:ConfigUuid | [FSM:STAGE:REMOTE-ERROR]: Configure logical UUID for server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:ConfigUuid) | warning | config-uuid-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateConfigUuid
F78413 | fsmRmtErrComputePhysicalAssociate:HbaImgUpdate | [FSM:STAGE:REMOTE-ERROR]: Update Host Bus Adapter image(FSM-STAGE:sam:dme:ComputePhysicalAssociate:HbaImgUpdate) | warning | hba-img-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateHbaImgUpdate
F78413 | fsmRmtErrComputePhysicalAssociate:HostOSConfig | [FSM:STAGE:REMOTE-ERROR]: Configure host OS components on server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:HostOSConfig) | warning | hostosconfig-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateHostOSConfig
F78413 | fsmRmtErrComputePhysicalAssociate:HostOSIdent | [FSM:STAGE:REMOTE-ERROR]: Identify host agent on server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:HostOSIdent) | warning | hostosident-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateHostOSIdent
F78413 | fsmRmtErrComputePhysicalAssociate:HostOSPolicy | [FSM:STAGE:REMOTE-ERROR]: Upload host agent policy to host agent on server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:HostOSPolicy) | warning | hostospolicy-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateHostOSPolicy
F78413 | fsmRmtErrComputePhysicalAssociate:HostOSValidate | [FSM:STAGE:REMOTE-ERROR]: Validate host OS on server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:HostOSValidate) | warning | hostosvalidate-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateHostOSValidate
F78413 | fsmRmtErrComputePhysicalAssociate:LocalDiskFwUpdate | [FSM:STAGE:REMOTE-ERROR]: Update LocalDisk firmware image(FSM-STAGE:sam:dme:ComputePhysicalAssociate:LocalDiskFwUpdate) | warning | local-disk-fw-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateLocalDiskFwUpdate
F78413 | fsmRmtErrComputePhysicalAssociate:NicConfigHostOSLocal | [FSM:STAGE:REMOTE-ERROR]: Configure adapter in server for host OS (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicConfigHostOSLocal) | warning | nic-config-hostoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateNicConfigHostOSLocal
F78413 | fsmRmtErrComputePhysicalAssociate:NicConfigHostOSPeer | [FSM:STAGE:REMOTE-ERROR]: Configure adapter in server for host OS (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicConfigHostOSPeer) | warning | nic-config-hostospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateNicConfigHostOSPeer
F78413 | fsmRmtErrComputePhysicalAssociate:NicConfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: Configure adapter for pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicConfigPnuOSLocal) | warning | nic-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateNicConfigPnuOSLocal
F78413 | fsmRmtErrComputePhysicalAssociate:NicConfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: Configure adapter for pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicConfigPnuOSPeer) | warning | nic-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateNicConfigPnuOSPeer
F78413 | fsmRmtErrComputePhysicalAssociate:NicImgUpdate | [FSM:STAGE:REMOTE-ERROR]: Update adapter image(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicImgUpdate) | warning | nic-img-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateNicImgUpdate
F78413 | fsmRmtErrComputePhysicalAssociate:NicUnconfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfigure adapter of server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicUnconfigPnuOSLocal) | warning | nic-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateNicUnconfigPnuOSLocal
F78413 | fsmRmtErrComputePhysicalAssociate:NicUnconfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfigure adapter of server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:NicUnconfigPnuOSPeer) | warning | nic-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateNicUnconfigPnuOSPeer
F78413 | fsmRmtErrComputePhysicalAssociate:PnuOSCatalog | [FSM:STAGE:REMOTE-ERROR]: Populate pre-boot catalog to server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSCatalog) | warning | pnuoscatalog-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePnuOSCatalog
F78413 | fsmRmtErrComputePhysicalAssociate:PnuOSConfig | [FSM:STAGE:REMOTE-ERROR]: Configure server with service profile [assignedToDn] pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSConfig) | warning | pnuosconfig-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePnuOSConfig
F78413 | fsmRmtErrComputePhysicalAssociate:PnuOSIdent | [FSM:STAGE:REMOTE-ERROR]: Identify pre-boot environment agent(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSIdent) | warning | pnuosident-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePnuOSIdent
F78413 | fsmRmtErrComputePhysicalAssociate:PnuOSInventory | [FSM:STAGE:REMOTE-ERROR]: Perform inventory of server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSInventory) | warning | pnuosinventory-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePnuOSInventory
F78413 | fsmRmtErrComputePhysicalAssociate:PnuOSLocalDiskConfig | [FSM:STAGE:REMOTE-ERROR]: Configure local disk on server with service profile [assignedToDn] pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSLocalDiskConfig) | warning | pnuoslocal-disk-config-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePnuOSLocalDiskConfig
F78413 | fsmRmtErrComputePhysicalAssociate:PnuOSPolicy | [FSM:STAGE:REMOTE-ERROR]: Populate pre-boot environment behavior policy(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSPolicy) | warning | pnuospolicy-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePnuOSPolicy
F78413 | fsmRmtErrComputePhysicalAssociate:PnuOSSelfTest | [FSM:STAGE:REMOTE-ERROR]: Trigger self-test on pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSSelfTest) | warning | pnuosself-test-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePnuOSSelfTest
F78413 | fsmRmtErrComputePhysicalAssociate:PnuOSUnloadDrivers | [FSM:STAGE:REMOTE-ERROR]: Unload drivers on server with service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSUnloadDrivers) | warning | pnuosunload-drivers-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePnuOSUnloadDrivers
F78413 | fsmRmtErrComputePhysicalAssociate:PnuOSValidate | [FSM:STAGE:REMOTE-ERROR]: Pre-boot environment validation for association with [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:PnuOSValidate) | warning | pnuosvalidate-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePnuOSValidate
F78413 | fsmRmtErrComputePhysicalAssociate:PollBiosActivateStatus | [FSM:STAGE:REMOTE-ERROR]: waiting for BIOS activate(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PollBiosActivateStatus) | warning | poll-bios-activate-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePollBiosActivateStatus
F78413 | fsmRmtErrComputePhysicalAssociate:PollBiosUpdateStatus | [FSM:STAGE:REMOTE-ERROR]: Waiting for BIOS update to complete(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PollBiosUpdateStatus) | warning | poll-bios-update-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePollBiosUpdateStatus
F78413 | fsmRmtErrComputePhysicalAssociate:PollBoardCtrlUpdateStatus | [FSM:STAGE:REMOTE-ERROR]: Waiting for Board Controller update to complete(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PollBoardCtrlUpdateStatus) | warning | poll-board-ctrl-update-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePollBoardCtrlUpdateStatus
F78413 | fsmRmtErrComputePhysicalAssociate:PollClearBiosUpdateStatus | [FSM:STAGE:REMOTE-ERROR]: waiting for pending BIOS image update to clear(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PollClearBiosUpdateStatus) | warning | poll-clear-bios-update-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePollClearBiosUpdateStatus
F78413 | fsmRmtErrComputePhysicalAssociate:PowerOn | [FSM:STAGE:REMOTE-ERROR]: Power on server for configuration of service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:PowerOn) | warning | power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePowerOn
F78413 | fsmRmtErrComputePhysicalAssociate:PreSanitize | [FSM:STAGE:REMOTE-ERROR]: Preparing to check hardware configuration(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePreSanitize
F78413 | fsmRmtErrComputePhysicalAssociate:PrepareForBoot | [FSM:STAGE:REMOTE-ERROR]: Prepare server for booting host OS(FSM-STAGE:sam:dme:ComputePhysicalAssociate:PrepareForBoot) | warning | prepare-for-boot-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociatePrepareForBoot
F78413 | fsmRmtErrComputePhysicalAssociate:Sanitize | [FSM:STAGE:REMOTE-ERROR]: Checking hardware configuration(FSM-STAGE:sam:dme:ComputePhysicalAssociate:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSanitize
F78413 | fsmRmtErrComputePhysicalAssociate:SolRedirectDisable | [FSM:STAGE:REMOTE-ERROR]: Disable Sol Redirection on server [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:SolRedirectDisable) | warning | sol-redirect-disable-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSolRedirectDisable
F78413 | fsmRmtErrComputePhysicalAssociate:SolRedirectEnable | [FSM:STAGE:REMOTE-ERROR]: set up bios token for server [assignedToDn] for Sol redirect(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SolRedirectEnable) | warning | sol-redirect-enable-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSolRedirectEnable
F78413 | fsmRmtErrComputePhysicalAssociate:StorageCtlrImgUpdate | [FSM:STAGE:REMOTE-ERROR]: Update storage controller image(FSM-STAGE:sam:dme:ComputePhysicalAssociate:StorageCtlrImgUpdate) | warning | storage-ctlr-img-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateStorageCtlrImgUpdate
F78413 | fsmRmtErrComputePhysicalAssociate:SwConfigHostOSLocal | [FSM:STAGE:REMOTE-ERROR]: Configure primary fabric interconnect for server host os (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigHostOSLocal) | warning | sw-config-hostoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSwConfigHostOSLocal
F78413 | fsmRmtErrComputePhysicalAssociate:SwConfigHostOSPeer | [FSM:STAGE:REMOTE-ERROR]: Configure secondary fabric interconnect for server host OS (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigHostOSPeer) | warning | sw-config-hostospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSwConfigHostOSPeer
F78413 | fsmRmtErrComputePhysicalAssociate:SwConfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: Configure primary fabric interconnect for pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigPnuOSLocal) | warning | sw-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSwConfigPnuOSLocal
F78413 | fsmRmtErrComputePhysicalAssociate:SwConfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: Configure secondary fabric interconnect for pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigPnuOSPeer) | warning | sw-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSwConfigPnuOSPeer
F78413 | fsmRmtErrComputePhysicalAssociate:SwConfigPortNivLocal | [FSM:STAGE:REMOTE-ERROR]: configuring primary fabric interconnect access to server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigPortNivLocal) | warning | sw-config-port-niv-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSwConfigPortNivLocal
F78413 | fsmRmtErrComputePhysicalAssociate:SwConfigPortNivPeer | [FSM:STAGE:REMOTE-ERROR]: configuring secondary fabric interconnect access to server(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwConfigPortNivPeer) | warning | sw-config-port-niv-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSwConfigPortNivPeer
F78413 | fsmRmtErrComputePhysicalAssociate:SwUnconfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfigure primary fabric interconnect for server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwUnconfigPnuOSLocal) | warning | sw-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSwUnconfigPnuOSLocal
F78413 | fsmRmtErrComputePhysicalAssociate:SwUnconfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfigure secondary fabric interconnect for server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalAssociate:SwUnconfigPnuOSPeer) | warning | sw-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSwUnconfigPnuOSPeer
F78413 | fsmRmtErrComputePhysicalAssociate:UpdateBiosRequest | [FSM:STAGE:REMOTE-ERROR]: Sending update BIOS request to CIMC(FSM-STAGE:sam:dme:ComputePhysicalAssociate:UpdateBiosRequest) | warning | update-bios-request-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateUpdateBiosRequest
F78413 | fsmRmtErrComputePhysicalAssociate:UpdateBoardCtrlRequest | [FSM:STAGE:REMOTE-ERROR]: Sending Board Controller update request to CIMC(FSM-STAGE:sam:dme:ComputePhysicalAssociate:UpdateBoardCtrlRequest) | warning | update-board-ctrl-request-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateUpdateBoardCtrlRequest
F78413 | fsmRmtErrComputePhysicalAssociate:activateAdaptorNwFwLocal | [FSM:STAGE:REMOTE-ERROR]: Activate adapter network firmware on(FSM-STAGE:sam:dme:ComputePhysicalAssociate:activateAdaptorNwFwLocal) | warning | activate-adaptor-nw-fw-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateActivateAdaptorNwFwLocal
F78413 | fsmRmtErrComputePhysicalAssociate:activateAdaptorNwFwPeer | [FSM:STAGE:REMOTE-ERROR]: Activate adapter network firmware on(FSM-STAGE:sam:dme:ComputePhysicalAssociate:activateAdaptorNwFwPeer) | warning | activate-adaptor-nw-fw-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateActivateAdaptorNwFwPeer
F78413 | fsmRmtErrComputePhysicalAssociate:activateIBMCFw | [FSM:STAGE:REMOTE-ERROR]: Activate CIMC firmware of server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:activateIBMCFw) | warning | activateibmcfw-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateActivateIBMCFw
F78413 | fsmRmtErrComputePhysicalAssociate:hagHostOSConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to host agent on server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalAssociate:hagHostOSConnect) | warning | hag-hostosconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateHagHostOSConnect
F78413 | fsmRmtErrComputePhysicalAssociate:hagPnuOSConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to pre-boot environment agent for association with [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:hagPnuOSConnect) | warning | hag-pnuosconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateHagPnuOSConnect
F78413 | fsmRmtErrComputePhysicalAssociate:hagPnuOSDisconnect | [FSM:STAGE:REMOTE-ERROR]: Disconnect pre-boot environment agent(FSM-STAGE:sam:dme:ComputePhysicalAssociate:hagPnuOSDisconnect) | warning | hag-pnuosdisconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateHagPnuOSDisconnect
F78413 | fsmRmtErrComputePhysicalAssociate:resetIBMC | [FSM:STAGE:REMOTE-ERROR]: Reset CIMC of server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:resetIBMC) | warning | resetibmc-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateResetIBMC
F78413 | fsmRmtErrComputePhysicalAssociate:serialDebugPnuOSConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to pre-boot environment agent for association with [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalAssociate:serialDebugPnuOSConnect) | warning | serial-debug-pnuosconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSerialDebugPnuOSConnect
F78413 | fsmRmtErrComputePhysicalAssociate:serialDebugPnuOSDisconnect | [FSM:STAGE:REMOTE-ERROR]: Disconnect pre-boot environment agent(FSM-STAGE:sam:dme:ComputePhysicalAssociate:serialDebugPnuOSDisconnect) | warning | serial-debug-pnuosdisconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateSerialDebugPnuOSDisconnect
F78413 | fsmRmtErrComputePhysicalAssociate:updateAdaptorNwFwLocal | [FSM:STAGE:REMOTE-ERROR]: Update adapter network firmware(FSM-STAGE:sam:dme:ComputePhysicalAssociate:updateAdaptorNwFwLocal) | warning | update-adaptor-nw-fw-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateUpdateAdaptorNwFwLocal
F78413 | fsmRmtErrComputePhysicalAssociate:updateAdaptorNwFwPeer | [FSM:STAGE:REMOTE-ERROR]: Update adapter network firmware(FSM-STAGE:sam:dme:ComputePhysicalAssociate:updateAdaptorNwFwPeer) | warning | update-adaptor-nw-fw-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateUpdateAdaptorNwFwPeer
F78413 | fsmRmtErrComputePhysicalAssociate:updateIBMCFw | [FSM:STAGE:REMOTE-ERROR]: Update CIMC firmware of server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:updateIBMCFw) | warning | updateibmcfw-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateUpdateIBMCFw
F78413 | fsmRmtErrComputePhysicalAssociate:waitForAdaptorNwFwUpdateLocal | [FSM:STAGE:REMOTE-ERROR]: Wait for adapter network firmware update completion(FSM-STAGE:sam:dme:ComputePhysicalAssociate:waitForAdaptorNwFwUpdateLocal) | warning | wait-for-adaptor-nw-fw-update-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateWaitForAdaptorNwFwUpdateLocal
F78413 | fsmRmtErrComputePhysicalAssociate:waitForAdaptorNwFwUpdatePeer | [FSM:STAGE:REMOTE-ERROR]: Wait for adapter network firmware update completion(FSM-STAGE:sam:dme:ComputePhysicalAssociate:waitForAdaptorNwFwUpdatePeer) | warning | wait-for-adaptor-nw-fw-update-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateWaitForAdaptorNwFwUpdatePeer
F78413 | fsmRmtErrComputePhysicalAssociate:waitForIBMCFwUpdate | [FSM:STAGE:REMOTE-ERROR]: Wait for CIMC firmware completion on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalAssociate:waitForIBMCFwUpdate) | warning | wait-foribmcfw-update-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78413 | fsmRmtErrComputePhysicalAssociateWaitForIBMCFwUpdate
F78414 | fsmRmtErrComputePhysicalDisassociate:BiosPostCompletion | [FSM:STAGE:REMOTE-ERROR]: Waiting for BIOS POST completion from CIMC on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BiosPostCompletion) | warning | bios-post-completion-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateBiosPostCompletion
F78414 | fsmRmtErrComputePhysicalDisassociate:BmcConfigPnuOS | [FSM:STAGE:REMOTE-ERROR]: provisioning a bootable device with a bootable pre-boot image for server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BmcConfigPnuOS) | warning | bmc-config-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateBmcConfigPnuOS
F78414 | fsmRmtErrComputePhysicalDisassociate:BmcPreconfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BmcPreconfigPnuOSLocal) | warning | bmc-preconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateBmcPreconfigPnuOSLocal
F78414 | fsmRmtErrComputePhysicalDisassociate:BmcPreconfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: prepare configuration for preboot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BmcPreconfigPnuOSPeer) | warning | bmc-preconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateBmcPreconfigPnuOSPeer
F78414 | fsmRmtErrComputePhysicalDisassociate:BmcUnconfigPnuOS | [FSM:STAGE:REMOTE-ERROR]: unprovisioning the bootable device for server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BmcUnconfigPnuOS) | warning | bmc-unconfig-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateBmcUnconfigPnuOS
F78414 | fsmRmtErrComputePhysicalDisassociate:BootPnuos | [FSM:STAGE:REMOTE-ERROR]: Bring-up pre-boot environment on server for disassociation with service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BootPnuos) | warning | boot-pnuos-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateBootPnuos
F78414 | fsmRmtErrComputePhysicalDisassociate:BootWait | [FSM:STAGE:REMOTE-ERROR]: Waiting for system reset on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:BootWait) | warning | boot-wait-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateBootWait
F78414 | fsmRmtErrComputePhysicalDisassociate:ConfigBios | [FSM:STAGE:REMOTE-ERROR]: Configuring BIOS Defaults on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:ConfigBios) | warning | config-bios-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateConfigBios
F78414 | fsmRmtErrComputePhysicalDisassociate:ConfigUserAccess | [FSM:STAGE:REMOTE-ERROR]: Configuring external user access(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:ConfigUserAccess) | warning | config-user-access-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateConfigUserAccess
F78414 | fsmRmtErrComputePhysicalDisassociate:HandlePooling | [FSM:STAGE:REMOTE-ERROR]: Apply post-disassociation policies to server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:HandlePooling) | warning | handle-pooling-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateHandlePooling
F78414 | fsmRmtErrComputePhysicalDisassociate:NicConfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: Configure adapter for pre-boot environment on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicConfigPnuOSLocal) | warning | nic-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateNicConfigPnuOSLocal
F78414 | fsmRmtErrComputePhysicalDisassociate:NicConfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: Configure adapter for pre-boot environment on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicConfigPnuOSPeer) | warning | nic-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateNicConfigPnuOSPeer
F78414 | fsmRmtErrComputePhysicalDisassociate:NicUnconfigHostOSLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfigure host OS connectivity from server adapter(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicUnconfigHostOSLocal) | warning | nic-unconfig-hostoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateNicUnconfigHostOSLocal
F78414 | fsmRmtErrComputePhysicalDisassociate:NicUnconfigHostOSPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfigure host OS connectivity from server adapter(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicUnconfigHostOSPeer) | warning | nic-unconfig-hostospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateNicUnconfigHostOSPeer
F78414 | fsmRmtErrComputePhysicalDisassociate:NicUnconfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfigure adapter of server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicUnconfigPnuOSLocal) | warning | nic-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateNicUnconfigPnuOSLocal
F78414 | fsmRmtErrComputePhysicalDisassociate:NicUnconfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfigure adapter of server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:NicUnconfigPnuOSPeer) | warning | nic-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateNicUnconfigPnuOSPeer
F78414 | fsmRmtErrComputePhysicalDisassociate:PnuOSCatalog | [FSM:STAGE:REMOTE-ERROR]: Populate pre-boot catalog to server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSCatalog) | warning | pnuoscatalog-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociatePnuOSCatalog
F78414 | fsmRmtErrComputePhysicalDisassociate:PnuOSIdent | [FSM:STAGE:REMOTE-ERROR]: Identify pre-boot environment agent on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSIdent) | warning | pnuosident-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociatePnuOSIdent
F78414 | fsmRmtErrComputePhysicalDisassociate:PnuOSPolicy | [FSM:STAGE:REMOTE-ERROR]: Populate pre-boot environment behavior policy to server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSPolicy) | warning | pnuospolicy-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociatePnuOSPolicy
F78414 | fsmRmtErrComputePhysicalDisassociate:PnuOSScrub | [FSM:STAGE:REMOTE-ERROR]: Scrub server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSScrub) | warning | pnuosscrub-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociatePnuOSScrub
F78414 | fsmRmtErrComputePhysicalDisassociate:PnuOSSelfTest | [FSM:STAGE:REMOTE-ERROR]: Trigger self-test of server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSSelfTest) | warning | pnuosself-test-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociatePnuOSSelfTest
F78414 | fsmRmtErrComputePhysicalDisassociate:PnuOSUnconfig | [FSM:STAGE:REMOTE-ERROR]: Unconfigure server from service profile [assignedToDn] pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSUnconfig) | warning | pnuosunconfig-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociatePnuOSUnconfig
F78414 | fsmRmtErrComputePhysicalDisassociate:PnuOSValidate | [FSM:STAGE:REMOTE-ERROR]: Pre-boot environment validate server for disassociation with service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PnuOSValidate) | warning | pnuosvalidate-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociatePnuOSValidate
F78414 | fsmRmtErrComputePhysicalDisassociate:PowerOn | [FSM:STAGE:REMOTE-ERROR]: Power on server for unconfiguration of service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PowerOn) | warning | power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociatePowerOn
F78414 | fsmRmtErrComputePhysicalDisassociate:PreSanitize | [FSM:STAGE:REMOTE-ERROR]: Preparing to check hardware configuration server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociatePreSanitize
F78414 | fsmRmtErrComputePhysicalDisassociate:Sanitize | [FSM:STAGE:REMOTE-ERROR]: Checking hardware configuration server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSanitize
F78414 | fsmRmtErrComputePhysicalDisassociate:Shutdown | [FSM:STAGE:REMOTE-ERROR]: Shutdown server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:Shutdown) | warning | shutdown-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateShutdown
F78414 | fsmRmtErrComputePhysicalDisassociate:SolRedirectDisable | [FSM:STAGE:REMOTE-ERROR]: Disable Sol redirection on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SolRedirectDisable) | warning | sol-redirect-disable-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSolRedirectDisable
F78414 | fsmRmtErrComputePhysicalDisassociate:SolRedirectEnable | [FSM:STAGE:REMOTE-ERROR]: set up bios token for server [serverId] for Sol redirect(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SolRedirectEnable) | warning | sol-redirect-enable-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSolRedirectEnable
F78414 | fsmRmtErrComputePhysicalDisassociate:SwConfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: Configure primary fabric interconnect for pre-boot environment on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwConfigPnuOSLocal) | warning | sw-config-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSwConfigPnuOSLocal
F78414 | fsmRmtErrComputePhysicalDisassociate:SwConfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: Configure secondary fabric interconnect for pre-boot environment on server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwConfigPnuOSPeer) | warning | sw-config-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSwConfigPnuOSPeer
F78414 | fsmRmtErrComputePhysicalDisassociate:SwConfigPortNivLocal | [FSM:STAGE:REMOTE-ERROR]: configuring primary fabric interconnect access to server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwConfigPortNivLocal) | warning | sw-config-port-niv-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSwConfigPortNivLocal
F78414 | fsmRmtErrComputePhysicalDisassociate:SwConfigPortNivPeer | [FSM:STAGE:REMOTE-ERROR]: configuring secondary fabric interconnect access to server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwConfigPortNivPeer) | warning | sw-config-port-niv-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSwConfigPortNivPeer
F78414 | fsmRmtErrComputePhysicalDisassociate:SwUnconfigHostOSLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfigure host OS connectivity from server to primary fabric interconnect(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwUnconfigHostOSLocal) | warning | sw-unconfig-hostoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSwUnconfigHostOSLocal
F78414 | fsmRmtErrComputePhysicalDisassociate:SwUnconfigHostOSPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfigure host OS connectivity from server to secondary fabric interconnect(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwUnconfigHostOSPeer) | warning | sw-unconfig-hostospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSwUnconfigHostOSPeer
F78414 | fsmRmtErrComputePhysicalDisassociate:SwUnconfigPnuOSLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfigure primary fabric interconnect for server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwUnconfigPnuOSLocal) | warning | sw-unconfig-pnuoslocal-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSwUnconfigPnuOSLocal
F78414 | fsmRmtErrComputePhysicalDisassociate:SwUnconfigPnuOSPeer | [FSM:STAGE:REMOTE-ERROR]: Unconfigure secondary fabric interconnect for server pre-boot environment(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:SwUnconfigPnuOSPeer) | warning | sw-unconfig-pnuospeer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSwUnconfigPnuOSPeer
F78414 | fsmRmtErrComputePhysicalDisassociate:UnconfigBios | [FSM:STAGE:REMOTE-ERROR]: Unconfiguring BIOS Settings and Boot Order of server [serverId] (service profile [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:UnconfigBios) | warning | unconfig-bios-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateUnconfigBios
F78414 | fsmRmtErrComputePhysicalDisassociate:UnconfigSoL | [FSM:STAGE:REMOTE-ERROR]: Removing SoL configuration from server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:UnconfigSoL) | warning | unconfig-so-lfailed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateUnconfigSoL
F78414 | fsmRmtErrComputePhysicalDisassociate:UnconfigUuid | [FSM:STAGE:REMOTE-ERROR]: Restore original UUID for server (service profile: [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:UnconfigUuid) | warning | unconfig-uuid-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateUnconfigUuid
F78414 | fsmRmtErrComputePhysicalDisassociate:hagPnuOSConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to pre-boot environment agent on server for disassociation with service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:hagPnuOSConnect) | warning | hag-pnuosconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateHagPnuOSConnect
F78414 | fsmRmtErrComputePhysicalDisassociate:hagPnuOSDisconnect | [FSM:STAGE:REMOTE-ERROR]: Disconnect pre-boot environment agent for server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:hagPnuOSDisconnect) | warning | hag-pnuosdisconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateHagPnuOSDisconnect
F78414 | fsmRmtErrComputePhysicalDisassociate:serialDebugPnuOSConnect | [FSM:STAGE:REMOTE-ERROR]: Connect to pre-boot environment agent on server for disassociation with service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalDisassociate:serialDebugPnuOSConnect) | warning | serial-debug-pnuosconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSerialDebugPnuOSConnect
F78414 | fsmRmtErrComputePhysicalDisassociate:serialDebugPnuOSDisconnect | [FSM:STAGE:REMOTE-ERROR]: Disconnect pre-boot environment agent for server(FSM-STAGE:sam:dme:ComputePhysicalDisassociate:serialDebugPnuOSDisconnect) | warning | serial-debug-pnuosdisconnect-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78414 | fsmRmtErrComputePhysicalDisassociateSerialDebugPnuOSDisconnect
F78416 | fsmRmtErrComputePhysicalDecommission:CleanupCIMC | [FSM:STAGE:REMOTE-ERROR]: Cleaning up CIMC configuration for server [dn](FSM-STAGE:sam:dme:ComputePhysicalDecommission:CleanupCIMC) | warning | cleanupcimc-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78416 | fsmRmtErrComputePhysicalDecommissionCleanupCIMC
F78416 | fsmRmtErrComputePhysicalDecommission:Execute | [FSM:STAGE:REMOTE-ERROR]: Decommissioning server [dn](FSM-STAGE:sam:dme:ComputePhysicalDecommission:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78416 | fsmRmtErrComputePhysicalDecommissionExecute
F78416 | fsmRmtErrComputePhysicalDecommission:StopVMediaLocal | [FSM:STAGE:REMOTE-ERROR]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalDecommission:StopVMediaLocal) | warning | stopvmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78416 | fsmRmtErrComputePhysicalDecommissionStopVMediaLocal
F78416 | fsmRmtErrComputePhysicalDecommission:StopVMediaPeer | [FSM:STAGE:REMOTE-ERROR]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalDecommission:StopVMediaPeer) | warning | stopvmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78416 | fsmRmtErrComputePhysicalDecommissionStopVMediaPeer
F78417 | fsmRmtErrComputePhysicalSoftShutdown:Execute | [FSM:STAGE:REMOTE-ERROR]: Soft shutdown of server [dn](FSM-STAGE:sam:dme:ComputePhysicalSoftShutdown:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78417 | fsmRmtErrComputePhysicalSoftShutdownExecute
F78418 | fsmRmtErrComputePhysicalHardShutdown:Execute | [FSM:STAGE:REMOTE-ERROR]: Hard shutdown of server [dn](FSM-STAGE:sam:dme:ComputePhysicalHardShutdown:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78418 | fsmRmtErrComputePhysicalHardShutdownExecute
F78419 | fsmRmtErrComputePhysicalTurnup:Execute | [FSM:STAGE:REMOTE-ERROR]: Power-on server [dn](FSM-STAGE:sam:dme:ComputePhysicalTurnup:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78419 | fsmRmtErrComputePhysicalTurnupExecute
F78420 | fsmRmtErrComputePhysicalPowercycle:Execute | [FSM:STAGE:REMOTE-ERROR]: Power-cycle server [dn](FSM-STAGE:sam:dme:ComputePhysicalPowercycle:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78420 | fsmRmtErrComputePhysicalPowercycleExecute
F78420 | fsmRmtErrComputePhysicalPowercycle:PreSanitize | [FSM:STAGE:REMOTE-ERROR]: Preparing to check hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalPowercycle:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78420 | fsmRmtErrComputePhysicalPowercyclePreSanitize
F78420 | fsmRmtErrComputePhysicalPowercycle:Sanitize | [FSM:STAGE:REMOTE-ERROR]: Checking hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalPowercycle:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78420 | fsmRmtErrComputePhysicalPowercycleSanitize
F78421 | fsmRmtErrComputePhysicalHardreset:Execute | [FSM:STAGE:REMOTE-ERROR]: Hard-reset server [dn](FSM-STAGE:sam:dme:ComputePhysicalHardreset:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78421 | fsmRmtErrComputePhysicalHardresetExecute
F78421 | fsmRmtErrComputePhysicalHardreset:PreSanitize | [FSM:STAGE:REMOTE-ERROR]: Preparing to check hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalHardreset:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78421 | fsmRmtErrComputePhysicalHardresetPreSanitize
F78421 | fsmRmtErrComputePhysicalHardreset:Sanitize | [FSM:STAGE:REMOTE-ERROR]: Checking hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalHardreset:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78421 | fsmRmtErrComputePhysicalHardresetSanitize
F78422 | fsmRmtErrComputePhysicalSoftreset:Execute | [FSM:STAGE:REMOTE-ERROR]: Soft-reset server [dn](FSM-STAGE:sam:dme:ComputePhysicalSoftreset:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78422 | fsmRmtErrComputePhysicalSoftresetExecute
F78422 | fsmRmtErrComputePhysicalSoftreset:PreSanitize | [FSM:STAGE:REMOTE-ERROR]: Preparing to check hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalSoftreset:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78422 | fsmRmtErrComputePhysicalSoftresetPreSanitize
F78422 | fsmRmtErrComputePhysicalSoftreset:Sanitize | [FSM:STAGE:REMOTE-ERROR]: Checking hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalSoftreset:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78422 | fsmRmtErrComputePhysicalSoftresetSanitize
F78423 | fsmRmtErrComputePhysicalSwConnUpd:A | [FSM:STAGE:REMOTE-ERROR]: Updating fabric A for server [dn](FSM-STAGE:sam:dme:ComputePhysicalSwConnUpd:A) | warning | a-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78423 | fsmRmtErrComputePhysicalSwConnUpdA
F78423 | fsmRmtErrComputePhysicalSwConnUpd:B | [FSM:STAGE:REMOTE-ERROR]: Updating fabric B for server [dn](FSM-STAGE:sam:dme:ComputePhysicalSwConnUpd:B) | warning | b-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78423 | fsmRmtErrComputePhysicalSwConnUpdB
F78424 | fsmRmtErrComputePhysicalBiosRecovery:Cleanup | [FSM:STAGE:REMOTE-ERROR]: Completing BIOS recovery mode for server [dn], and shutting it down(FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Cleanup) | warning | cleanup-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoveryCleanup
F78424 | fsmRmtErrComputePhysicalBiosRecovery:PreSanitize | [FSM:STAGE:REMOTE-ERROR]: Preparing to check hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoveryPreSanitize
F78424 | fsmRmtErrComputePhysicalBiosRecovery:Reset | [FSM:STAGE:REMOTE-ERROR]: Resetting server [dn] power state after BIOS recovery(FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Reset) | warning | reset-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoveryReset
F78424 | fsmRmtErrComputePhysicalBiosRecovery:Sanitize | [FSM:STAGE:REMOTE-ERROR]: Checking hardware configuration server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoverySanitize
F78424 | fsmRmtErrComputePhysicalBiosRecovery:SetupVmediaLocal | [FSM:STAGE:REMOTE-ERROR]: Provisioning a V-Media device with a bootable BIOS image for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:SetupVmediaLocal) | warning | setup-vmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoverySetupVmediaLocal
F78424 | fsmRmtErrComputePhysicalBiosRecovery:SetupVmediaPeer | [FSM:STAGE:REMOTE-ERROR]: Provisioning a V-Media device with a bootable BIOS image for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:SetupVmediaPeer) | warning | setup-vmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoverySetupVmediaPeer
F78424 | fsmRmtErrComputePhysicalBiosRecovery:Shutdown | [FSM:STAGE:REMOTE-ERROR]: Shutting down server [dn] to prepare for BIOS recovery(FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Shutdown) | warning | shutdown-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoveryShutdown
F78424 | fsmRmtErrComputePhysicalBiosRecovery:Start | [FSM:STAGE:REMOTE-ERROR]: Running BIOS recovery on server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Start) | warning | start-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoveryStart
F78424 | fsmRmtErrComputePhysicalBiosRecovery:StopVMediaLocal | [FSM:STAGE:REMOTE-ERROR]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:StopVMediaLocal) | warning | stopvmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoveryStopVMediaLocal
F78424 | fsmRmtErrComputePhysicalBiosRecovery:StopVMediaPeer | [FSM:STAGE:REMOTE-ERROR]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:StopVMediaPeer) | warning | stopvmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoveryStopVMediaPeer
F78424 | fsmRmtErrComputePhysicalBiosRecovery:TeardownVmediaLocal | [FSM:STAGE:REMOTE-ERROR]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:TeardownVmediaLocal) | warning | teardown-vmedia-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoveryTeardownVmediaLocal
F78424 | fsmRmtErrComputePhysicalBiosRecovery:TeardownVmediaPeer | [FSM:STAGE:REMOTE-ERROR]: Unprovisioning the V-Media bootable device for server [dn](FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:TeardownVmediaPeer) | warning | teardown-vmedia-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoveryTeardownVmediaPeer
F78424 | fsmRmtErrComputePhysicalBiosRecovery:Wait | [FSM:STAGE:REMOTE-ERROR]: Waiting for completion of BIOS recovery for server [dn] (up to 15 min)(FSM-STAGE:sam:dme:ComputePhysicalBiosRecovery:Wait) | warning | wait-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78424 | fsmRmtErrComputePhysicalBiosRecoveryWait
F78426 | fsmRmtErrComputePhysicalCmosReset:BladePowerOn | [FSM:STAGE:REMOTE-ERROR]: Power on server [serverId](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:BladePowerOn) | warning | blade-power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78426 | fsmRmtErrComputePhysicalCmosResetBladePowerOn
F78426 | fsmRmtErrComputePhysicalCmosReset:Execute | [FSM:STAGE:REMOTE-ERROR]: Resetting CMOS for server [serverId](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78426 | fsmRmtErrComputePhysicalCmosResetExecute
F78426 | fsmRmtErrComputePhysicalCmosReset:PreSanitize | [FSM:STAGE:REMOTE-ERROR]: Preparing to check hardware configuration server [serverId](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:PreSanitize) | warning | pre-sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78426 | fsmRmtErrComputePhysicalCmosResetPreSanitize
F78426 | fsmRmtErrComputePhysicalCmosReset:ReconfigBios | [FSM:STAGE:REMOTE-ERROR]: Reconfiguring BIOS Settings and Boot Order of server [serverId] for service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:ReconfigBios) | warning | reconfig-bios-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78426 | fsmRmtErrComputePhysicalCmosResetReconfigBios
F78426 | fsmRmtErrComputePhysicalCmosReset:ReconfigUuid | [FSM:STAGE:REMOTE-ERROR]: Reconfiguring logical UUID of server [serverId] for service profile [assignedToDn](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:ReconfigUuid) | warning | reconfig-uuid-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78426 | fsmRmtErrComputePhysicalCmosResetReconfigUuid
F78426 | fsmRmtErrComputePhysicalCmosReset:Sanitize | [FSM:STAGE:REMOTE-ERROR]: Checking hardware configuration server [serverId](FSM-STAGE:sam:dme:ComputePhysicalCmosReset:Sanitize) | warning | sanitize-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78426 | fsmRmtErrComputePhysicalCmosResetSanitize
F78427 | fsmRmtErrComputePhysicalResetBmc:Execute | [FSM:STAGE:REMOTE-ERROR]: Resetting Management Controller on server [dn](FSM-STAGE:sam:dme:ComputePhysicalResetBmc:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78427 | fsmRmtErrComputePhysicalResetBmcExecute
F78428 | fsmRmtErrEquipmentIOCardResetIom:Execute | [FSM:STAGE:REMOTE-ERROR]: Reset IOM [id] on Fex [chassisId](FSM-STAGE:sam:dme:EquipmentIOCardResetIom:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 78428 | fsmRmtErrEquipmentIOCardResetIomExecute
F78448 | fsmRmtErrComputePhysicalUpdateExtUsers:Deploy | [FSM:STAGE:REMOTE-ERROR]: external mgmt user deployment on server [dn] (profile [assignedToDn])(FSM-STAGE:sam:dme:ComputePhysicalUpdateExtUsers:Deploy) | warning | deploy-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78448 | fsmRmtErrComputePhysicalUpdateExtUsersDeploy
F78452 | fsmRmtErrSysdebugTechSupportInitiate:Local | [FSM:STAGE:REMOTE-ERROR]: create tech-support file from GUI on local(FSM-STAGE:sam:dme:SysdebugTechSupportInitiate:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 78452 | fsmRmtErrSysdebugTechSupportInitiateLocal
F78453 | fsmRmtErrSysdebugTechSupportDeleteTechSupFile:Local | [FSM:STAGE:REMOTE-ERROR]: delete tech-support file from GUI on local(FSM-STAGE:sam:dme:SysdebugTechSupportDeleteTechSupFile:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 78453 | fsmRmtErrSysdebugTechSupportDeleteTechSupFileLocal
F78453 | fsmRmtErrSysdebugTechSupportDeleteTechSupFile:peer | [FSM:STAGE:REMOTE-ERROR]: delete tech-support file from GUI on peer(FSM-STAGE:sam:dme:SysdebugTechSupportDeleteTechSupFile:peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 78453 | fsmRmtErrSysdebugTechSupportDeleteTechSupFilePeer
F78454 | fsmRmtErrFirmwareDownloaderDownload:CopyRemote | [FSM:STAGE:REMOTE-ERROR]: sync images to subordinate(FSM-STAGE:sam:dme:FirmwareDownloaderDownload:CopyRemote) | warning | copy-remote-failed | None set. | None set. | none | TRUE | fsm | firmware:Downloader | sys/fw-catalogue/dnld-[fileName] | 78454 | fsmRmtErrFirmwareDownloaderDownloadCopyRemote
F78454 | fsmRmtErrFirmwareDownloaderDownload:DeleteLocal | [FSM:STAGE:REMOTE-ERROR]: deleting downloadable [fileName] on local(FSM-STAGE:sam:dme:FirmwareDownloaderDownload:DeleteLocal) | warning | delete-local-failed | None set. | None set. | none | TRUE | fsm | firmware:Downloader | sys/fw-catalogue/dnld-[fileName] | 78454 | fsmRmtErrFirmwareDownloaderDownloadDeleteLocal
F78454 | fsmRmtErrFirmwareDownloaderDownload:Local | [FSM:STAGE:REMOTE-ERROR]: downloading image [fileName] from [server](FSM-STAGE:sam:dme:FirmwareDownloaderDownload:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | firmware:Downloader | sys/fw-catalogue/dnld-[fileName] | 78454 | fsmRmtErrFirmwareDownloaderDownloadLocal
F78454 | fsmRmtErrFirmwareDownloaderDownload:UnpackLocal | [FSM:STAGE:REMOTE-ERROR]: unpacking image [fileName] on primary(FSM-STAGE:sam:dme:FirmwareDownloaderDownload:UnpackLocal) | warning | unpack-local-failed | None set. | None set. | none | TRUE | fsm | firmware:Downloader | sys/fw-catalogue/dnld-[fileName] | 78454 | fsmRmtErrFirmwareDownloaderDownloadUnpackLocal
F78454 | fsmRmtErrLicenseDownloaderDownload:CopyRemote | [FSM:STAGE:REMOTE-ERROR]: Copy the license file to subordinate for inventory(FSM-STAGE:sam:dme:LicenseDownloaderDownload:CopyRemote) | warning | copy-remote-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 78454 | fsmRmtErrLicenseDownloaderDownloadCopyRemote
F78454 | fsmRmtErrLicenseDownloaderDownload:DeleteLocal | [FSM:STAGE:REMOTE-ERROR]: deleting temporary files for [fileName] on local(FSM-STAGE:sam:dme:LicenseDownloaderDownload:DeleteLocal) | warning | delete-local-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 78454 | fsmRmtErrLicenseDownloaderDownloadDeleteLocal
F78454 | fsmRmtErrLicenseDownloaderDownload:DeleteRemote | [FSM:STAGE:REMOTE-ERROR]: deleting temporary files for [fileName] on subordinate(FSM-STAGE:sam:dme:LicenseDownloaderDownload:DeleteRemote) | warning | delete-remote-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 78454 | fsmRmtErrLicenseDownloaderDownloadDeleteRemote
F78454 | fsmRmtErrLicenseDownloaderDownload:Local | [FSM:STAGE:REMOTE-ERROR]: downloading license file [fileName] from [server](FSM-STAGE:sam:dme:LicenseDownloaderDownload:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 78454 | fsmRmtErrLicenseDownloaderDownloadLocal
F78454 | fsmRmtErrLicenseDownloaderDownload:ValidateLocal | [FSM:STAGE:REMOTE-ERROR]: validation for license file [fileName] on primary(FSM-STAGE:sam:dme:LicenseDownloaderDownload:ValidateLocal) | warning | validate-local-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 78454 | fsmRmtErrLicenseDownloaderDownloadValidateLocal
F78454 | fsmRmtErrLicenseDownloaderDownload:ValidateRemote | [FSM:STAGE:REMOTE-ERROR]: validation for license file [fileName] on subordinate(FSM-STAGE:sam:dme:LicenseDownloaderDownload:ValidateRemote) | warning | validate-remote-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 78454 | fsmRmtErrLicenseDownloaderDownloadValidateRemote
F78454 | fsmRmtErrSysdebugCoreDownload:CopyPrimary | [FSM:STAGE:REMOTE-ERROR]: Copy the Core file to primary for download(FSM-STAGE:sam:dme:SysdebugCoreDownload:CopyPrimary) | warning | copy-primary-failed | None set. | None set. | none | TRUE | fsm | sysdebug:Core | sys/corefiles/file-[name]¦[switchId] | 78454 | fsmRmtErrSysdebugCoreDownloadCopyPrimary
F78454 | fsmRmtErrSysdebugCoreDownload:CopySub | [FSM:STAGE:REMOTE-ERROR]: copy Core file on subordinate switch to tmp directory(FSM-STAGE:sam:dme:SysdebugCoreDownload:CopySub) | warning | copy-sub-failed | None set. | None set. | none | TRUE | fsm | sysdebug:Core | sys/corefiles/file-[name]¦[switchId] | 78454 | fsmRmtErrSysdebugCoreDownloadCopySub
F78454 | fsmRmtErrSysdebugCoreDownload:DeletePrimary | [FSM:STAGE:REMOTE-ERROR]: Delete the Core file from primary switch under tmp directory(FSM-STAGE:sam:dme:SysdebugCoreDownload:DeletePrimary) | warning | delete-primary-failed | None set. | None set. | none | TRUE | fsm | sysdebug:Core | sys/corefiles/file-[name]¦[switchId] | 78454 | fsmRmtErrSysdebugCoreDownloadDeletePrimary
F78454 | fsmRmtErrSysdebugCoreDownload:DeleteSub | [FSM:STAGE:REMOTE-ERROR]: Delete the Core file from subordinate under tmp directory(FSM-STAGE:sam:dme:SysdebugCoreDownload:DeleteSub) | warning | delete-sub-failed | None set. | None set. | none | TRUE | fsm | sysdebug:Core | sys/corefiles/file-[name]¦[switchId] | 78454 | fsmRmtErrSysdebugCoreDownloadDeleteSub
F78454 | fsmRmtErrSysdebugTechSupportDownload:CopyPrimary | [FSM:STAGE:REMOTE-ERROR]: Copy the tech-support file to primary for download(FSM-STAGE:sam:dme:SysdebugTechSupportDownload:CopyPrimary) | warning | copy-primary-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 78454 | fsmRmtErrSysdebugTechSupportDownloadCopyPrimary
F78454 | fsmRmtErrSysdebugTechSupportDownload:CopySub | [FSM:STAGE:REMOTE-ERROR]: copy tech-support file on subordinate switch to tmp directory(FSM-STAGE:sam:dme:SysdebugTechSupportDownload:CopySub) | warning | copy-sub-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 78454 | fsmRmtErrSysdebugTechSupportDownloadCopySub
F78454 | fsmRmtErrSysdebugTechSupportDownload:DeletePrimary | [FSM:STAGE:REMOTE-ERROR]: Delete the tech-support file from primary switch under tmp directory(FSM-STAGE:sam:dme:SysdebugTechSupportDownload:DeletePrimary) | warning | delete-primary-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 78454 | fsmRmtErrSysdebugTechSupportDownloadDeletePrimary
F78454 | fsmRmtErrSysdebugTechSupportDownload:DeleteSub | [FSM:STAGE:REMOTE-ERROR]: Delete the tech-support file from subordinate under tmp directory(FSM-STAGE:sam:dme:SysdebugTechSupportDownload:DeleteSub) | warning | delete-sub-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 78454 | fsmRmtErrSysdebugTechSupportDownloadDeleteSub
F78483 | fsmRmtErrComputePhysicalUpdateAdaptor:PollUpdateStatusLocal | [FSM:STAGE:REMOTE-ERROR]: waiting for update to complete(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:PollUpdateStatusLocal) | warning | poll-update-status-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78483 | fsmRmtErrComputePhysicalUpdateAdaptorPollUpdateStatusLocal
F78483 | fsmRmtErrComputePhysicalUpdateAdaptor:PollUpdateStatusPeer | [FSM:STAGE:REMOTE-ERROR]: waiting for update to complete(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:PollUpdateStatusPeer) | warning | poll-update-status-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78483 | fsmRmtErrComputePhysicalUpdateAdaptorPollUpdateStatusPeer
F78483 | fsmRmtErrComputePhysicalUpdateAdaptor:PowerOff | [FSM:STAGE:REMOTE-ERROR]: Power off the server(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:PowerOff) | warning | power-off-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78483 | fsmRmtErrComputePhysicalUpdateAdaptorPowerOff
F78483 | fsmRmtErrComputePhysicalUpdateAdaptor:PowerOn | [FSM:STAGE:REMOTE-ERROR]: power on the blade(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:PowerOn) | warning | power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78483 | fsmRmtErrComputePhysicalUpdateAdaptorPowerOn
F78483 | fsmRmtErrComputePhysicalUpdateAdaptor:UpdateRequestLocal | [FSM:STAGE:REMOTE-ERROR]: sending update request to Adaptor(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:UpdateRequestLocal) | warning | update-request-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78483 | fsmRmtErrComputePhysicalUpdateAdaptorUpdateRequestLocal
F78483 | fsmRmtErrComputePhysicalUpdateAdaptor:UpdateRequestPeer | [FSM:STAGE:REMOTE-ERROR]: sending update request to Adaptor(FSM-STAGE:sam:dme:ComputePhysicalUpdateAdaptor:UpdateRequestPeer) | warning | update-request-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78483 | fsmRmtErrComputePhysicalUpdateAdaptorUpdateRequestPeer
F78484 | fsmRmtErrComputePhysicalActivateAdaptor:ActivateLocal | [FSM:STAGE:REMOTE-ERROR]: activating backup image of Adaptor(FSM-STAGE:sam:dme:ComputePhysicalActivateAdaptor:ActivateLocal) | warning | activate-local-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78484 | fsmRmtErrComputePhysicalActivateAdaptorActivateLocal
F78484 | fsmRmtErrComputePhysicalActivateAdaptor:ActivatePeer | [FSM:STAGE:REMOTE-ERROR]: activating backup image of Adaptor(FSM-STAGE:sam:dme:ComputePhysicalActivateAdaptor:ActivatePeer) | warning | activate-peer-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78484 | fsmRmtErrComputePhysicalActivateAdaptorActivatePeer
F78484 | fsmRmtErrComputePhysicalActivateAdaptor:PowerOn | [FSM:STAGE:REMOTE-ERROR]: power on the blade(FSM-STAGE:sam:dme:ComputePhysicalActivateAdaptor:PowerOn) | warning | power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78484 | fsmRmtErrComputePhysicalActivateAdaptorPowerOn
F78484 | fsmRmtErrComputePhysicalActivateAdaptor:Reset | [FSM:STAGE:REMOTE-ERROR]: reseting the blade(FSM-STAGE:sam:dme:ComputePhysicalActivateAdaptor:Reset) | warning | reset-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78484 | fsmRmtErrComputePhysicalActivateAdaptorReset
F78485 | fsmRmtErrCapabilityCatalogueActivateCatalog:ApplyCatalog | [FSM:STAGE:REMOTE-ERROR]: applying changes to catalog(FSM-STAGE:sam:dme:CapabilityCatalogueActivateCatalog:ApplyCatalog) | warning | apply-catalog-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78485 | fsmRmtErrCapabilityCatalogueActivateCatalogApplyCatalog
F78485 | fsmRmtErrCapabilityCatalogueActivateCatalog:CopyRemote | [FSM:STAGE:REMOTE-ERROR]: syncing catalog changes to subordinate(FSM-STAGE:sam:dme:CapabilityCatalogueActivateCatalog:CopyRemote) | warning | copy-remote-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78485 | fsmRmtErrCapabilityCatalogueActivateCatalogCopyRemote
F78485 | fsmRmtErrCapabilityCatalogueActivateCatalog:EvaluateStatus | [FSM:STAGE:REMOTE-ERROR]: evaluating status of activation(FSM-STAGE:sam:dme:CapabilityCatalogueActivateCatalog:EvaluateStatus) | warning | evaluate-status-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78485 | fsmRmtErrCapabilityCatalogueActivateCatalogEvaluateStatus
F78485 | fsmRmtErrCapabilityCatalogueActivateCatalog:RescanImages | [FSM:STAGE:REMOTE-ERROR]: rescanning image files(FSM-STAGE:sam:dme:CapabilityCatalogueActivateCatalog:RescanImages) | warning | rescan-images-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78485 | fsmRmtErrCapabilityCatalogueActivateCatalogRescanImages
F78485 | fsmRmtErrCapabilityCatalogueActivateCatalog:UnpackLocal | [FSM:STAGE:REMOTE-ERROR]: activating catalog changes(FSM-STAGE:sam:dme:CapabilityCatalogueActivateCatalog:UnpackLocal) | warning | unpack-local-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 78485 | fsmRmtErrCapabilityCatalogueActivateCatalogUnpackLocal
F78486 | fsmRmtErrCapabilityMgmtExtensionActivateMgmtExt:ApplyCatalog | [FSM:STAGE:REMOTE-ERROR]: applying changes to catalog(FSM-STAGE:sam:dme:CapabilityMgmtExtensionActivateMgmtExt:ApplyCatalog) | warning | apply-catalog-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 78486 | fsmRmtErrCapabilityMgmtExtensionActivateMgmtExtApplyCatalog
F78486 | fsmRmtErrCapabilityMgmtExtensionActivateMgmtExt:CopyRemote | [FSM:STAGE:REMOTE-ERROR]: syncing management extension changes to subordinate(FSM-STAGE:sam:dme:CapabilityMgmtExtensionActivateMgmtExt:CopyRemote) | warning | copy-remote-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 78486 | fsmRmtErrCapabilityMgmtExtensionActivateMgmtExtCopyRemote
F78486 | fsmRmtErrCapabilityMgmtExtensionActivateMgmtExt:EvaluateStatus | [FSM:STAGE:REMOTE-ERROR]: evaluating status of activation(FSM-STAGE:sam:dme:CapabilityMgmtExtensionActivateMgmtExt:EvaluateStatus) | warning | evaluate-status-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 78486 | fsmRmtErrCapabilityMgmtExtensionActivateMgmtExtEvaluateStatus
F78486 | fsmRmtErrCapabilityMgmtExtensionActivateMgmtExt:RescanImages | [FSM:STAGE:REMOTE-ERROR]: rescanning image files(FSM-STAGE:sam:dme:CapabilityMgmtExtensionActivateMgmtExt:RescanImages) | warning | rescan-images-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 78486 | fsmRmtErrCapabilityMgmtExtensionActivateMgmtExtRescanImages
F78486 | fsmRmtErrCapabilityMgmtExtensionActivateMgmtExt:UnpackLocal | [FSM:STAGE:REMOTE-ERROR]: activating management extension changes(FSM-STAGE:sam:dme:CapabilityMgmtExtensionActivateMgmtExt:UnpackLocal) | warning | unpack-local-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 78486 | fsmRmtErrCapabilityMgmtExtensionActivateMgmtExtUnpackLocal
F78491 | fsmRmtErrLicenseFileInstall:Local | [FSM:STAGE:REMOTE-ERROR]: Installing license on primary(FSM-STAGE:sam:dme:LicenseFileInstall:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | license:File | sys/license/file-[scope]:[id] | 78491 | fsmRmtErrLicenseFileInstallLocal
F78491 | fsmRmtErrLicenseFileInstall:Remote | [FSM:STAGE:REMOTE-ERROR]: Installing license on subordinate(FSM-STAGE:sam:dme:LicenseFileInstall:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | license:File | sys/license/file-[scope]:[id] | 78491 | fsmRmtErrLicenseFileInstallRemote
F78492 | fsmRmtErrLicenseFileClear:Local | [FSM:STAGE:REMOTE-ERROR]: Clearing license on primary(FSM-STAGE:sam:dme:LicenseFileClear:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | license:File | sys/license/file-[scope]:[id] | 78492 | fsmRmtErrLicenseFileClearLocal
F78492 | fsmRmtErrLicenseFileClear:Remote | [FSM:STAGE:REMOTE-ERROR]: Clearing license on subordinate(FSM-STAGE:sam:dme:LicenseFileClear:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | license:File | sys/license/file-[scope]:[id] | 78492 | fsmRmtErrLicenseFileClearRemote
F78493 | fsmRmtErrLicenseInstanceUpdateFlexlm:Local | [FSM:STAGE:REMOTE-ERROR]: Updating on primary(FSM-STAGE:sam:dme:LicenseInstanceUpdateFlexlm:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 78493 | fsmRmtErrLicenseInstanceUpdateFlexlmLocal
F78493 | fsmRmtErrLicenseInstanceUpdateFlexlm:Remote | [FSM:STAGE:REMOTE-ERROR]: Updating on subordinate(FSM-STAGE:sam:dme:LicenseInstanceUpdateFlexlm:Remote) | warning | remote-failed | None set. | None set. | none | TRUE | fsm | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 78493 | fsmRmtErrLicenseInstanceUpdateFlexlmRemote
F78523 | fsmRmtErrComputePhysicalConfigSoL:Execute | [FSM:STAGE:REMOTE-ERROR]: configuring SoL interface on server [dn](FSM-STAGE:sam:dme:ComputePhysicalConfigSoL:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78523 | fsmRmtErrComputePhysicalConfigSoLExecute
F78524 | fsmRmtErrComputePhysicalUnconfigSoL:Execute | [FSM:STAGE:REMOTE-ERROR]: removing SoL interface configuration from server [dn](FSM-STAGE:sam:dme:ComputePhysicalUnconfigSoL:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78524 | fsmRmtErrComputePhysicalUnconfigSoLExecute
F78529 | fsmRmtErrPortPIoInCompatSfpPresence:Shutdown | [FSM:STAGE:REMOTE-ERROR]: Shutting down port(FSM-STAGE:sam:dme:PortPIoInCompatSfpPresence:Shutdown) | warning | shutdown-failed | None set. | None set. | none | TRUE | fsm | port:PIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 78529 | fsmRmtErrPortPIoInCompatSfpPresenceShutdown
F78556 | fsmRmtErrComputePhysicalDiagnosticInterrupt:Execute | [FSM:STAGE:REMOTE-ERROR]: Execute Diagnostic Interrupt(NMI) for server [dn](FSM-STAGE:sam:dme:ComputePhysicalDiagnosticInterrupt:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78556 | fsmRmtErrComputePhysicalDiagnosticInterruptExecute
F78574 | fsmRmtErrEquipmentChassisDynamicReallocation:Config | [FSM:STAGE:REMOTE-ERROR]: (FSM-STAGE:sam:dme:EquipmentChassisDynamicReallocation:Config) | warning | config-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 78574 | fsmRmtErrEquipmentChassisDynamicReallocationConfig
F78603 | fsmRmtErrComputePhysicalResetKvm:Execute | [FSM:STAGE:REMOTE-ERROR]: Execute KVM Reset for server [dn](FSM-STAGE:sam:dme:ComputePhysicalResetKvm:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78603 | fsmRmtErrComputePhysicalResetKvmExecute
F78609 | fsmRmtErrMgmtControllerOnline:BmcConfigureConnLocal | [FSM:STAGE:REMOTE-ERROR]: Configuring connectivity on CIMC(FSM-STAGE:sam:dme:MgmtControllerOnline:BmcConfigureConnLocal) | warning | bmc-configure-conn-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78609 | fsmRmtErrMgmtControllerOnlineBmcConfigureConnLocal
F78609 | fsmRmtErrMgmtControllerOnline:BmcConfigureConnPeer | [FSM:STAGE:REMOTE-ERROR]: Configuring connectivity on CIMC(FSM-STAGE:sam:dme:MgmtControllerOnline:BmcConfigureConnPeer) | warning | bmc-configure-conn-peer-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78609 | fsmRmtErrMgmtControllerOnlineBmcConfigureConnPeer
F78609 | fsmRmtErrMgmtControllerOnline:SwConfigureConnLocal | [FSM:STAGE:REMOTE-ERROR]: Configuring fabric-interconnect connectivity to CIMC(FSM-STAGE:sam:dme:MgmtControllerOnline:SwConfigureConnLocal) | warning | sw-configure-conn-local-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78609 | fsmRmtErrMgmtControllerOnlineSwConfigureConnLocal
F78609 | fsmRmtErrMgmtControllerOnline:SwConfigureConnPeer | [FSM:STAGE:REMOTE-ERROR]: Configuring fabric-interconnect connectivity to CIMC(FSM-STAGE:sam:dme:MgmtControllerOnline:SwConfigureConnPeer) | warning | sw-configure-conn-peer-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 78609 | fsmRmtErrMgmtControllerOnlineSwConfigureConnPeer
F78610 | fsmRmtErrComputeRackUnitOffline:CleanupLocal | [FSM:STAGE:REMOTE-ERROR]: cleaning host entries on local fabric-interconnect(FSM-STAGE:sam:dme:ComputeRackUnitOffline:CleanupLocal) | warning | cleanup-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 78610 | fsmRmtErrComputeRackUnitOfflineCleanupLocal
F78610 | fsmRmtErrComputeRackUnitOffline:CleanupPeer | [FSM:STAGE:REMOTE-ERROR]: cleaning host entries on peer fabric-interconnect(FSM-STAGE:sam:dme:ComputeRackUnitOffline:CleanupPeer) | warning | cleanup-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 78610 | fsmRmtErrComputeRackUnitOfflineCleanupPeer
F78610 | fsmRmtErrComputeRackUnitOffline:SwUnconfigureLocal | [FSM:STAGE:REMOTE-ERROR]: Unconfiguring fabric-interconnect connectivity to CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitOffline:SwUnconfigureLocal) | warning | sw-unconfigure-local-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 78610 | fsmRmtErrComputeRackUnitOfflineSwUnconfigureLocal
F78610 | fsmRmtErrComputeRackUnitOffline:SwUnconfigurePeer | [FSM:STAGE:REMOTE-ERROR]: Unconfiguring fabric-interconnect connectivity to CIMC of server [id](FSM-STAGE:sam:dme:ComputeRackUnitOffline:SwUnconfigurePeer) | warning | sw-unconfigure-peer-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 78610 | fsmRmtErrComputeRackUnitOfflineSwUnconfigurePeer
F78627 | fsmRmtErrEquipmentLocatorLedSetFiLocatorLed:Execute | [FSM:STAGE:REMOTE-ERROR]: setting FI locator led to [adminState](FSM-STAGE:sam:dme:EquipmentLocatorLedSetFiLocatorLed:Execute) | warning | execute-failed | None set. | None set. | none | TRUE | fsm | equipment:LocatorLed | sys/chassis-[id]/blade-[slotId]/locator-led | 78627 | fsmRmtErrEquipmentLocatorLedSetFiLocatorLedExecute
F78663 | fsmRmtErrVnicProfileSetDeployAlias:Local | [FSM:STAGE:REMOTE-ERROR]: VNIC profile alias configuration on local fabric(FSM-STAGE:sam:dme:VnicProfileSetDeployAlias:Local) | warning | local-failed | None set. | None set. | none | TRUE | fsm | vnic:ProfileSet | fabric/lan/profiles | 78663 | fsmRmtErrVnicProfileSetDeployAliasLocal
F78663 | fsmRmtErrVnicProfileSetDeployAlias:Peer | [FSM:STAGE:REMOTE-ERROR]: VNIC profile alias configuration on peer fabric(FSM-STAGE:sam:dme:VnicProfileSetDeployAlias:Peer) | warning | peer-failed | None set. | None set. | none | TRUE | fsm | vnic:ProfileSet | fabric/lan/profiles | 78663 | fsmRmtErrVnicProfileSetDeployAliasPeer
F78679 | fsmRmtErrSwPhysConfPhysical:ConfigSwA | [FSM:STAGE:REMOTE-ERROR]: Configure physical port types on fabric interconnect [id](FSM-STAGE:sam:dme:SwPhysConfPhysical:ConfigSwA) | warning | config-sw-afailed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 78679 | fsmRmtErrSwPhysConfPhysicalConfigSwA
F78679 | fsmRmtErrSwPhysConfPhysical:ConfigSwB | [FSM:STAGE:REMOTE-ERROR]: Configure physical port types on fabric interconnect [id](FSM-STAGE:sam:dme:SwPhysConfPhysical:ConfigSwB) | warning | config-sw-bfailed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 78679 | fsmRmtErrSwPhysConfPhysicalConfigSwB
F78679 | fsmRmtErrSwPhysConfPhysical:PortInventorySwA | [FSM:STAGE:REMOTE-ERROR]: Performing local port inventory of switch [id](FSM-STAGE:sam:dme:SwPhysConfPhysical:PortInventorySwA) | warning | port-inventory-sw-afailed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 78679 | fsmRmtErrSwPhysConfPhysicalPortInventorySwA
F78679 | fsmRmtErrSwPhysConfPhysical:PortInventorySwB | [FSM:STAGE:REMOTE-ERROR]: Performing peer port inventory of switch [id](FSM-STAGE:sam:dme:SwPhysConfPhysical:PortInventorySwB) | warning | port-inventory-sw-bfailed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 78679 | fsmRmtErrSwPhysConfPhysicalPortInventorySwB
F78679 | fsmRmtErrSwPhysConfPhysical:VerifyPhysConfig | [FSM:STAGE:REMOTE-ERROR]: Verifying physical transition on fabric interconnect [id](FSM-STAGE:sam:dme:SwPhysConfPhysical:VerifyPhysConfig) | warning | verify-phys-config-failed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 78679 | fsmRmtErrSwPhysConfPhysicalVerifyPhysConfig
F78694 | fsmRmtErrExtvmmEpClusterRole:SetLocal | [FSM:STAGE:REMOTE-ERROR]: external VM management cluster role configuration on local fabric(FSM-STAGE:sam:dme:ExtvmmEpClusterRole:SetLocal) | warning | set-local-failed | None set. | None set. | none | TRUE | fsm | extvmm:Ep | sys/extvm-mgmt | 78694 | fsmRmtErrExtvmmEpClusterRoleSetLocal
F78694 | fsmRmtErrExtvmmEpClusterRole:SetPeer | [FSM:STAGE:REMOTE-ERROR]: external VM management cluster role configuration on peer fabric(FSM-STAGE:sam:dme:ExtvmmEpClusterRole:SetPeer) | warning | set-peer-failed | None set. | None set. | none | TRUE | fsm | extvmm:Ep | sys/extvm-mgmt | 78694 | fsmRmtErrExtvmmEpClusterRoleSetPeer
F78702 | fsmRmtErrEquipmentBeaconLedIlluminate:ExecuteA | [FSM:STAGE:REMOTE-ERROR]: Turn beacon lights on/off for [dn] on fabric interconnect [id](FSM-STAGE:sam:dme:EquipmentBeaconLedIlluminate:ExecuteA) | warning | execute-afailed | None set. | None set. | none | TRUE | fsm | equipment:BeaconLed | sys/chassis-[id]/blade-[slotId]/beacon | 78702 | fsmRmtErrEquipmentBeaconLedIlluminateExecuteA
F78702 | fsmRmtErrEquipmentBeaconLedIlluminate:ExecuteB | [FSM:STAGE:REMOTE-ERROR]: Turn beacon lights on/off for [dn] on fabric interconnect [id](FSM-STAGE:sam:dme:EquipmentBeaconLedIlluminate:ExecuteB) | warning | execute-bfailed | None set. | None set. | none | TRUE | fsm | equipment:BeaconLed | sys/chassis-[id]/blade-[slotId]/beacon | 78702 | fsmRmtErrEquipmentBeaconLedIlluminateExecuteB
F78711 | fsmRmtErrEtherServerIntFIoConfigSpeed:Configure | [FSM:STAGE:REMOTE-ERROR]: Configure admin speed for [dn](FSM-STAGE:sam:dme:EtherServerIntFIoConfigSpeed:Configure) | warning | configure-failed | None set. | None set. | none | TRUE | fsm | ether:ServerIntFIo | sys/chassis-[id]/blade-[slotId]/diag/port-[portId] | 78711 | fsmRmtErrEtherServerIntFIoConfigSpeedConfigure
F78721 | fsmRmtErrComputePhysicalUpdateBIOS:Clear | [FSM:STAGE:REMOTE-ERROR]: clearing pending BIOS image update(FSM-STAGE:sam:dme:ComputePhysicalUpdateBIOS:Clear) | warning | clear-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78721 | fsmRmtErrComputePhysicalUpdateBIOSClear
F78721 | fsmRmtErrComputePhysicalUpdateBIOS:PollClearStatus | [FSM:STAGE:REMOTE-ERROR]: waiting for pending BIOS image update to clear(FSM-STAGE:sam:dme:ComputePhysicalUpdateBIOS:PollClearStatus) | warning | poll-clear-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78721 | fsmRmtErrComputePhysicalUpdateBIOSPollClearStatus
F78721 | fsmRmtErrComputePhysicalUpdateBIOS:PollUpdateStatus | [FSM:STAGE:REMOTE-ERROR]: waiting for BIOS update to complete(FSM-STAGE:sam:dme:ComputePhysicalUpdateBIOS:PollUpdateStatus) | warning | poll-update-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78721 | fsmRmtErrComputePhysicalUpdateBIOSPollUpdateStatus
F78721 | fsmRmtErrComputePhysicalUpdateBIOS:UpdateRequest | [FSM:STAGE:REMOTE-ERROR]: sending BIOS update request to CIMC(FSM-STAGE:sam:dme:ComputePhysicalUpdateBIOS:UpdateRequest) | warning | update-request-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78721 | fsmRmtErrComputePhysicalUpdateBIOSUpdateRequest
F78722 | fsmRmtErrComputePhysicalActivateBIOS:Activate | [FSM:STAGE:REMOTE-ERROR]: activating BIOS image(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:Activate) | warning | activate-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78722 | fsmRmtErrComputePhysicalActivateBIOSActivate
F78722 | fsmRmtErrComputePhysicalActivateBIOS:Clear | [FSM:STAGE:REMOTE-ERROR]: clearing pending BIOS image activate(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:Clear) | warning | clear-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78722 | fsmRmtErrComputePhysicalActivateBIOSClear
F78722 | fsmRmtErrComputePhysicalActivateBIOS:PollActivateStatus | [FSM:STAGE:REMOTE-ERROR]: waiting for BIOS activate(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:PollActivateStatus) | warning | poll-activate-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78722 | fsmRmtErrComputePhysicalActivateBIOSPollActivateStatus
F78722 | fsmRmtErrComputePhysicalActivateBIOS:PollClearStatus | [FSM:STAGE:REMOTE-ERROR]: waiting for pending BIOS image activate to clear(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:PollClearStatus) | warning | poll-clear-status-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78722 | fsmRmtErrComputePhysicalActivateBIOSPollClearStatus
F78722 | fsmRmtErrComputePhysicalActivateBIOS:PowerOff | [FSM:STAGE:REMOTE-ERROR]: Power off the server(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:PowerOff) | warning | power-off-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78722 | fsmRmtErrComputePhysicalActivateBIOSPowerOff
F78722 | fsmRmtErrComputePhysicalActivateBIOS:PowerOn | [FSM:STAGE:REMOTE-ERROR]: power on the server(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:PowerOn) | warning | power-on-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78722 | fsmRmtErrComputePhysicalActivateBIOSPowerOn
F78722 | fsmRmtErrComputePhysicalActivateBIOS:UpdateTokens | [FSM:STAGE:REMOTE-ERROR]: updating BIOS tokens(FSM-STAGE:sam:dme:ComputePhysicalActivateBIOS:UpdateTokens) | warning | update-tokens-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 78722 | fsmRmtErrComputePhysicalActivateBIOSUpdateTokens
F999445 | fsmFailEquipmentIOCardFePresence | [FSM:FAILED]: sam:dme:EquipmentIOCardFePresence | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 999445 | fsmFailEquipmentIOCardFePresence
F999446 | fsmFailEquipmentIOCardFeConn | [FSM:FAILED]: sam:dme:EquipmentIOCardFeConn | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 999446 | fsmFailEquipmentIOCardFeConn
F999447 | fsmFailEquipmentChassisRemoveChassis | [FSM:FAILED]: sam:dme:EquipmentChassisRemoveChassis | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 999447 | fsmFailEquipmentChassisRemoveChassis
F999448 | fsmFailEquipmentLocatorLedSetLocatorLed | [FSM:FAILED]: sam:dme:EquipmentLocatorLedSetLocatorLed | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:LocatorLed | sys/chassis-[id]/blade-[slotId]/locator-led | 999448 | fsmFailEquipmentLocatorLedSetLocatorLed
F999558 | fsmFailMgmtControllerExtMgmtIfConfig | [FSM:FAILED]: sam:dme:MgmtControllerExtMgmtIfConfig | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 999558 | fsmFailMgmtControllerExtMgmtIfConfig
F999559 | fsmFailFabricComputeSlotEpIdentify | [FSM:FAILED]: sam:dme:FabricComputeSlotEpIdentify | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | fabric:ComputeSlotEp | fabric/server/chassis-[chassisId]/slot-[slotId] | 999559 | fsmFailFabricComputeSlotEpIdentify
F999560 | fsmFailComputeBladeDiscover | [FSM:FAILED]: sam:dme:ComputeBladeDiscover | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 999560 | fsmFailComputeBladeDiscover
F999560 | fsmFailComputeRackUnitDiscover | [FSM:FAILED]: sam:dme:ComputeRackUnitDiscover | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 999560 | fsmFailComputeRackUnitDiscover
F999573 | fsmFailEquipmentChassisPsuPolicyConfig | [FSM:FAILED]: sam:dme:EquipmentChassisPsuPolicyConfig | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 999573 | fsmFailEquipmentChassisPsuPolicyConfig
F999574 | fsmFailAdaptorHostFcIfResetFcPersBinding | [FSM:FAILED]: sam:dme:AdaptorHostFcIfResetFcPersBinding | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 999574 | fsmFailAdaptorHostFcIfResetFcPersBinding
F999575 | fsmFailComputeBladeDiag | [FSM:FAILED]: sam:dme:ComputeBladeDiag | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 999575 | fsmFailComputeBladeDiag
F999579 | fsmFailFabricLanCloudSwitchMode | [FSM:FAILED]: sam:dme:FabricLanCloudSwitchMode | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | fabric:LanCloud | fabric/lan | 999579 | fsmFailFabricLanCloudSwitchMode
F999579 | fsmFailFabricSanCloudSwitchMode | [FSM:FAILED]: sam:dme:FabricSanCloudSwitchMode | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | fabric:SanCloud | fabric/san | 999579 | fsmFailFabricSanCloudSwitchMode
F999616 | fsmFailCommSvcEpUpdateSvcEp | [FSM:FAILED]: sam:dme:CommSvcEpUpdateSvcEp | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 999616 | fsmFailCommSvcEpUpdateSvcEp
F999617 | fsmFailCommSvcEpRestartWebSvc | [FSM:FAILED]: sam:dme:CommSvcEpRestartWebSvc | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | comm:SvcEp | sys/svc-ext | 999617 | fsmFailCommSvcEpRestartWebSvc
F999619 | fsmFailAaaEpUpdateEp | [FSM:FAILED]: sam:dme:AaaEpUpdateEp | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | aaa:Ep | sys/ | 999619 | fsmFailAaaEpUpdateEp
F999619 | fsmFailPkiEpUpdateEp | [FSM:FAILED]: sam:dme:PkiEpUpdateEp | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | pki:Ep | sys/pki-ext | 999619 | fsmFailPkiEpUpdateEp
F999619 | fsmFailStatsCollectionPolicyUpdateEp | [FSM:FAILED]: sam:dme:StatsCollectionPolicyUpdateEp | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | stats:CollectionPolicy | stats/coll-policy-[name] | 999619 | fsmFailStatsCollectionPolicyUpdateEp
F999620 | fsmFailAaaRealmUpdateRealm | [FSM:FAILED]: sam:dme:AaaRealmUpdateRealm | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | aaa:Realm | sys/ | 999620 | fsmFailAaaRealmUpdateRealm
F999621 | fsmFailAaaUserEpUpdateUserEp | [FSM:FAILED]: sam:dme:AaaUserEpUpdateUserEp | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | aaa:UserEp | sys/user-ext | 999621 | fsmFailAaaUserEpUpdateUserEp
F999640 | fsmFailSysfileMutationSingle | [FSM:FAILED]: sam:dme:SysfileMutationSingle | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sysfile:Mutation | sys/corefiles/file-[name]¦[switchId]/mutation | 999640 | fsmFailSysfileMutationSingle
F999641 | fsmFailSysfileMutationGlobal | [FSM:FAILED]: sam:dme:SysfileMutationGlobal | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sysfile:Mutation | sys/corefiles/file-[name]¦[switchId]/mutation | 999641 | fsmFailSysfileMutationGlobal
F999644 | fsmFailSysdebugManualCoreFileExportTargetExport | [FSM:FAILED]: sam:dme:SysdebugManualCoreFileExportTargetExport | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sysdebug:ManualCoreFileExportTarget | sys/corefiles/file-[name]¦[switchId]/export-to-[hostname] | 999644 | fsmFailSysdebugManualCoreFileExportTargetExport
F999645 | fsmFailFabricEpMgrConfigure | [FSM:FAILED]: sam:dme:FabricEpMgrConfigure | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | fabric:EpMgr | fabric/[id] | 999645 | fsmFailFabricEpMgrConfigure
F999645 | fsmFailLsServerConfigure | [FSM:FAILED]: sam:dme:LsServerConfigure | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | ls:Server | org-[name]/tier-[name]/ls-[name] | 999645 | fsmFailLsServerConfigure
F999645 | fsmFailSysdebugAutoCoreFileExportTargetConfigure | [FSM:FAILED]: sam:dme:SysdebugAutoCoreFileExportTargetConfigure | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sysdebug:AutoCoreFileExportTarget | sys/sysdebug/file-export | 999645 | fsmFailSysdebugAutoCoreFileExportTargetConfigure
F999646 | fsmFailSysdebugLogControlEpLogControlPersist | [FSM:FAILED]: sam:dme:SysdebugLogControlEpLogControlPersist | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sysdebug:LogControlEp | sys/sysdebug/logcontrol | 999646 | fsmFailSysdebugLogControlEpLogControlPersist
F999674 | fsmFailEpqosDefinitionDeploy | [FSM:FAILED]: sam:dme:EpqosDefinitionDeploy | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | epqos:Definition | org-[name]/ep-qos-[name] | 999674 | fsmFailEpqosDefinitionDeploy
F999674 | fsmFailSwAccessDomainDeploy | [FSM:FAILED]: sam:dme:SwAccessDomainDeploy | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sw:AccessDomain | sys/switch-[id]/access-eth | 999674 | fsmFailSwAccessDomainDeploy
F999674 | fsmFailSwEthLanBorderDeploy | [FSM:FAILED]: sam:dme:SwEthLanBorderDeploy | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sw:EthLanBorder | sys/switch-[id]/border-eth | 999674 | fsmFailSwEthLanBorderDeploy
F999674 | fsmFailSwEthMonDeploy | [FSM:FAILED]: sam:dme:SwEthMonDeploy | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sw:EthMon | sys/switch-[id]/lanmon-eth/mon-[name] | 999674 | fsmFailSwEthMonDeploy
F999674 | fsmFailSwFcMonDeploy | [FSM:FAILED]: sam:dme:SwFcMonDeploy | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sw:FcMon | sys/switch-[id]/sanmon-fc/mon-[name] | 999674 | fsmFailSwFcMonDeploy
F999674 | fsmFailSwFcSanBorderDeploy | [FSM:FAILED]: sam:dme:SwFcSanBorderDeploy | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sw:FcSanBorder | sys/switch-[id]/border-fc | 999674 | fsmFailSwFcSanBorderDeploy
F999674 | fsmFailSwUtilityDomainDeploy | [FSM:FAILED]: sam:dme:SwUtilityDomainDeploy | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sw:UtilityDomain | sys/switch-[id]/utility-eth | 999674 | fsmFailSwUtilityDomainDeploy
F999674 | fsmFailVnicProfileSetDeploy | [FSM:FAILED]: sam:dme:VnicProfileSetDeploy | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | vnic:ProfileSet | fabric/lan/profiles | 999674 | fsmFailVnicProfileSetDeploy
F999681 | fsmFailSyntheticFsObjCreate | [FSM:FAILED]: sam:dme:SyntheticFsObjCreate | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | synthetic:FsObj | sys/file-[name] | 999681 | fsmFailSyntheticFsObjCreate
F999691 | fsmFailFirmwareDistributableDelete | [FSM:FAILED]: sam:dme:FirmwareDistributableDelete | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | firmware:Distributable | sys/fw-catalogue/distrib-[name] | 999691 | fsmFailFirmwareDistributableDelete
F999691 | fsmFailFirmwareImageDelete | [FSM:FAILED]: sam:dme:FirmwareImageDelete | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | firmware:Image | sys/fw-catalogue/image-[name] | 999691 | fsmFailFirmwareImageDelete
F999693 | fsmFailMgmtControllerUpdateSwitch | [FSM:FAILED]: sam:dme:MgmtControllerUpdateSwitch | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 999693 | fsmFailMgmtControllerUpdateSwitch
F999694 | fsmFailMgmtControllerUpdateIOM | [FSM:FAILED]: sam:dme:MgmtControllerUpdateIOM | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 999694 | fsmFailMgmtControllerUpdateIOM
F999695 | fsmFailMgmtControllerActivateIOM | [FSM:FAILED]: sam:dme:MgmtControllerActivateIOM | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 999695 | fsmFailMgmtControllerActivateIOM
F999696 | fsmFailMgmtControllerUpdateBMC | [FSM:FAILED]: sam:dme:MgmtControllerUpdateBMC | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 999696 | fsmFailMgmtControllerUpdateBMC
F999697 | fsmFailMgmtControllerActivateBMC | [FSM:FAILED]: sam:dme:MgmtControllerActivateBMC | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 999697 | fsmFailMgmtControllerActivateBMC
F999710 | fsmFailCallhomeEpConfigCallhome | [FSM:FAILED]: sam:dme:CallhomeEpConfigCallhome | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | callhome:Ep | call-home | 999710 | fsmFailCallhomeEpConfigCallhome
F999713 | fsmFailMgmtIfSwMgmtOobIfConfig | [FSM:FAILED]: sam:dme:MgmtIfSwMgmtOobIfConfig | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 999713 | fsmFailMgmtIfSwMgmtOobIfConfig
F999714 | fsmFailMgmtIfSwMgmtInbandIfConfig | [FSM:FAILED]: sam:dme:MgmtIfSwMgmtInbandIfConfig | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 999714 | fsmFailMgmtIfSwMgmtInbandIfConfig
F999719 | fsmFailMgmtIfVirtualIfConfig | [FSM:FAILED]: sam:dme:MgmtIfVirtualIfConfig | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 999719 | fsmFailMgmtIfVirtualIfConfig
F999720 | fsmFailMgmtIfEnableVip | [FSM:FAILED]: sam:dme:MgmtIfEnableVip | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 999720 | fsmFailMgmtIfEnableVip
F999721 | fsmFailMgmtIfDisableVip | [FSM:FAILED]: sam:dme:MgmtIfDisableVip | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 999721 | fsmFailMgmtIfDisableVip
F999722 | fsmFailMgmtIfEnableHA | [FSM:FAILED]: sam:dme:MgmtIfEnableHA | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:If | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id]/if-[id] | 999722 | fsmFailMgmtIfEnableHA
F999723 | fsmFailMgmtBackupBackup | [FSM:FAILED]: sam:dme:MgmtBackupBackup | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Backup | sys/backup-[hostname] | 999723 | fsmFailMgmtBackupBackup
F999724 | fsmFailMgmtImporterImport | [FSM:FAILED]: sam:dme:MgmtImporterImport | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Importer | sys/import-config-[hostname] | 999724 | fsmFailMgmtImporterImport
F999785 | fsmFailQosclassDefinitionConfigGlobalQoS | [FSM:FAILED]: sam:dme:QosclassDefinitionConfigGlobalQoS | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | qosclass:Definition | fabric/lan/classes | 999785 | fsmFailQosclassDefinitionConfigGlobalQoS
F999790 | fsmFailEpqosDefinitionDelTaskRemove | [FSM:FAILED]: sam:dme:EpqosDefinitionDelTaskRemove | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | epqos:DefinitionDelTask | org-[name]/ep-qos-deletion-[defIntId] | 999790 | fsmFailEpqosDefinitionDelTaskRemove
F999843 | fsmFailEquipmentIOCardResetCmc | [FSM:FAILED]: sam:dme:EquipmentIOCardResetCmc | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 999843 | fsmFailEquipmentIOCardResetCmc
F999855 | fsmFailMgmtControllerUpdateUCSManager | [FSM:FAILED]: sam:dme:MgmtControllerUpdateUCSManager | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 999855 | fsmFailMgmtControllerUpdateUCSManager
F999863 | fsmFailMgmtControllerSysConfig | [FSM:FAILED]: sam:dme:MgmtControllerSysConfig | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 999863 | fsmFailMgmtControllerSysConfig
F999892 | fsmFailAdaptorExtEthIfPathReset | [FSM:FAILED]: sam:dme:AdaptorExtEthIfPathReset | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | adaptor:ExtEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/ext-eth-[id] | 999892 | fsmFailAdaptorExtEthIfPathReset
F999897 | fsmFailAdaptorHostEthIfCircuitReset | [FSM:FAILED]: sam:dme:AdaptorHostEthIfCircuitReset | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | adaptor:HostEthIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-eth-[id] | 999897 | fsmFailAdaptorHostEthIfCircuitReset
F999897 | fsmFailAdaptorHostFcIfCircuitReset | [FSM:FAILED]: sam:dme:AdaptorHostFcIfCircuitReset | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | adaptor:HostFcIf | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/host-fc-[id] | 999897 | fsmFailAdaptorHostFcIfCircuitReset
F999919 | fsmFailExtvmmMasterExtKeyConfig | [FSM:FAILED]: sam:dme:ExtvmmMasterExtKeyConfig | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | extvmm:MasterExtKey | sys/extvm-mgmt/ext-key | 999919 | fsmFailExtvmmMasterExtKeyConfig
F999919 | fsmFailExtvmmProviderConfig | [FSM:FAILED]: sam:dme:ExtvmmProviderConfig | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | extvmm:Provider | sys/extvm-mgmt/vm-[name] | 999919 | fsmFailExtvmmProviderConfig
F999919 | fsmFailVmLifeCyclePolicyConfig | [FSM:FAILED]: sam:dme:VmLifeCyclePolicyConfig | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | vm:LifeCyclePolicy | org-[name]/vm-lc-policy | 999919 | fsmFailVmLifeCyclePolicyConfig
F999920 | fsmFailExtvmmKeyStoreCertInstall | [FSM:FAILED]: sam:dme:ExtvmmKeyStoreCertInstall | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | extvmm:KeyStore | sys/extvm-mgmt/key-store | 999920 | fsmFailExtvmmKeyStoreCertInstall
F999921 | fsmFailExtvmmSwitchDelTaskRemoveProvider | [FSM:FAILED]: sam:dme:ExtvmmSwitchDelTaskRemoveProvider | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | extvmm:SwitchDelTask | sys/extvm-mgmt/vsw-deltask-[swIntId] | 999921 | fsmFailExtvmmSwitchDelTaskRemoveProvider
F999944 | fsmFailCapabilityUpdaterUpdater | [FSM:FAILED]: sam:dme:CapabilityUpdaterUpdater | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | capability:Updater | capabilities/ep/updater-[fileName] | 999944 | fsmFailCapabilityUpdaterUpdater
F999970 | fsmFailComputeBladeUpdateBoardController | [FSM:FAILED]: sam:dme:ComputeBladeUpdateBoardController | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Blade | sys/chassis-[id]/blade-[slotId] | 999970 | fsmFailComputeBladeUpdateBoardController
F999971 | fsmFailCapabilityCatalogueDeployCatalogue | [FSM:FAILED]: sam:dme:CapabilityCatalogueDeployCatalogue | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 999971 | fsmFailCapabilityCatalogueDeployCatalogue
F999982 | fsmFailEquipmentFexRemoveFex | [FSM:FAILED]: sam:dme:EquipmentFexRemoveFex | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:Fex | sys/fex-[id] | 999982 | fsmFailEquipmentFexRemoveFex
F999983 | fsmFailEquipmentLocatorLedSetFeLocatorLed | [FSM:FAILED]: sam:dme:EquipmentLocatorLedSetFeLocatorLed | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:LocatorLed | sys/chassis-[id]/blade-[slotId]/locator-led | 999983 | fsmFailEquipmentLocatorLedSetFeLocatorLed
F999984 | fsmFailComputePhysicalPowerCap | [FSM:FAILED]: sam:dme:ComputePhysicalPowerCap | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 999984 | fsmFailComputePhysicalPowerCap
F999984 | fsmFailEquipmentChassisPowerCap | [FSM:FAILED]: sam:dme:EquipmentChassisPowerCap | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 999984 | fsmFailEquipmentChassisPowerCap
F999985 | fsmFailEquipmentIOCardMuxOffline | [FSM:FAILED]: sam:dme:EquipmentIOCardMuxOffline | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 999985 | fsmFailEquipmentIOCardMuxOffline
F1000013 | fsmFailComputePhysicalAssociate | [FSM:FAILED]: sam:dme:ComputePhysicalAssociate | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000013 | fsmFailComputePhysicalAssociate
F1000014 | fsmFailComputePhysicalDisassociate | [FSM:FAILED]: sam:dme:ComputePhysicalDisassociate | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000014 | fsmFailComputePhysicalDisassociate
F1000016 | fsmFailComputePhysicalDecommission | [FSM:FAILED]: sam:dme:ComputePhysicalDecommission | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000016 | fsmFailComputePhysicalDecommission
F1000017 | fsmFailComputePhysicalSoftShutdown | [FSM:FAILED]: sam:dme:ComputePhysicalSoftShutdown | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000017 | fsmFailComputePhysicalSoftShutdown
F1000018 | fsmFailComputePhysicalHardShutdown | [FSM:FAILED]: sam:dme:ComputePhysicalHardShutdown | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000018 | fsmFailComputePhysicalHardShutdown
F1000019 | fsmFailComputePhysicalTurnup | [FSM:FAILED]: sam:dme:ComputePhysicalTurnup | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000019 | fsmFailComputePhysicalTurnup
F1000020 | fsmFailComputePhysicalPowercycle | [FSM:FAILED]: sam:dme:ComputePhysicalPowercycle | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000020 | fsmFailComputePhysicalPowercycle
F1000021 | fsmFailComputePhysicalHardreset | [FSM:FAILED]: sam:dme:ComputePhysicalHardreset | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000021 | fsmFailComputePhysicalHardreset
F1000022 | fsmFailComputePhysicalSoftreset | [FSM:FAILED]: sam:dme:ComputePhysicalSoftreset | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000022 | fsmFailComputePhysicalSoftreset
F1000023 | fsmFailComputePhysicalSwConnUpd | [FSM:FAILED]: sam:dme:ComputePhysicalSwConnUpd | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000023 | fsmFailComputePhysicalSwConnUpd
F1000024 | fsmFailComputePhysicalBiosRecovery | [FSM:FAILED]: sam:dme:ComputePhysicalBiosRecovery | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000024 | fsmFailComputePhysicalBiosRecovery
F1000026 | fsmFailComputePhysicalCmosReset | [FSM:FAILED]: sam:dme:ComputePhysicalCmosReset | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000026 | fsmFailComputePhysicalCmosReset
F1000027 | fsmFailComputePhysicalResetBmc | [FSM:FAILED]: sam:dme:ComputePhysicalResetBmc | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000027 | fsmFailComputePhysicalResetBmc
F1000028 | fsmFailEquipmentIOCardResetIom | [FSM:FAILED]: sam:dme:EquipmentIOCardResetIom | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:IOCard | sys/chassis-[id]/slot-[id] | 1000028 | fsmFailEquipmentIOCardResetIom
F1000048 | fsmFailComputePhysicalUpdateExtUsers | [FSM:FAILED]: sam:dme:ComputePhysicalUpdateExtUsers | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000048 | fsmFailComputePhysicalUpdateExtUsers
F1000052 | fsmFailSysdebugTechSupportInitiate | [FSM:FAILED]: sam:dme:SysdebugTechSupportInitiate | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 1000052 | fsmFailSysdebugTechSupportInitiate
F1000053 | fsmFailSysdebugTechSupportDeleteTechSupFile | [FSM:FAILED]: sam:dme:SysdebugTechSupportDeleteTechSupFile | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 1000053 | fsmFailSysdebugTechSupportDeleteTechSupFile
F1000054 | fsmFailFirmwareDownloaderDownload | [FSM:FAILED]: sam:dme:FirmwareDownloaderDownload | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | firmware:Downloader | sys/fw-catalogue/dnld-[fileName] | 1000054 | fsmFailFirmwareDownloaderDownload
F1000054 | fsmFailLicenseDownloaderDownload | [FSM:FAILED]: sam:dme:LicenseDownloaderDownload | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | license:Downloader | sys/license/dnld-[fileName] | 1000054 | fsmFailLicenseDownloaderDownload
F1000054 | fsmFailSysdebugCoreDownload | [FSM:FAILED]: sam:dme:SysdebugCoreDownload | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sysdebug:Core | sys/corefiles/file-[name]¦[switchId] | 1000054 | fsmFailSysdebugCoreDownload
F1000054 | fsmFailSysdebugTechSupportDownload | [FSM:FAILED]: sam:dme:SysdebugTechSupportDownload | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sysdebug:TechSupport | sys/tech-support-files/tech-support-[creationTS] | 1000054 | fsmFailSysdebugTechSupportDownload
F1000083 | fsmFailComputePhysicalUpdateAdaptor | [FSM:FAILED]: sam:dme:ComputePhysicalUpdateAdaptor | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000083 | fsmFailComputePhysicalUpdateAdaptor
F1000084 | fsmFailComputePhysicalActivateAdaptor | [FSM:FAILED]: sam:dme:ComputePhysicalActivateAdaptor | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000084 | fsmFailComputePhysicalActivateAdaptor
F1000085 | fsmFailCapabilityCatalogueActivateCatalog | [FSM:FAILED]: sam:dme:CapabilityCatalogueActivateCatalog | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | capability:Catalogue | capabilities | 1000085 | fsmFailCapabilityCatalogueActivateCatalog
F1000086 | fsmFailCapabilityMgmtExtensionActivateMgmtExt | [FSM:FAILED]: sam:dme:CapabilityMgmtExtensionActivateMgmtExt | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | capability:MgmtExtension | capabilities/ep/mgmt-ext | 1000086 | fsmFailCapabilityMgmtExtensionActivateMgmtExt
F1000091 | fsmFailLicenseFileInstall | [FSM:FAILED]: sam:dme:LicenseFileInstall | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | license:File | sys/license/file-[scope]:[id] | 1000091 | fsmFailLicenseFileInstall
F1000092 | fsmFailLicenseFileClear | [FSM:FAILED]: sam:dme:LicenseFileClear | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | license:File | sys/license/file-[scope]:[id] | 1000092 | fsmFailLicenseFileClear
F1000093 | fsmFailLicenseInstanceUpdateFlexlm | [FSM:FAILED]: sam:dme:LicenseInstanceUpdateFlexlm | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | license:Instance | sys/license/feature-[name]-[vendor]-[version]/inst-[scope] | 1000093 | fsmFailLicenseInstanceUpdateFlexlm
F1000123 | fsmFailComputePhysicalConfigSoL | [FSM:FAILED]: sam:dme:ComputePhysicalConfigSoL | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000123 | fsmFailComputePhysicalConfigSoL
F1000124 | fsmFailComputePhysicalUnconfigSoL | [FSM:FAILED]: sam:dme:ComputePhysicalUnconfigSoL | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000124 | fsmFailComputePhysicalUnconfigSoL
F1000129 | fsmFailPortPIoInCompatSfpPresence | [FSM:FAILED]: sam:dme:PortPIoInCompatSfpPresence | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | port:PIo | sys/chassis-[id]/slot-[id]/[type]/port-[portId] | 1000129 | fsmFailPortPIoInCompatSfpPresence
F1000156 | fsmFailComputePhysicalDiagnosticInterrupt | [FSM:FAILED]: sam:dme:ComputePhysicalDiagnosticInterrupt | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000156 | fsmFailComputePhysicalDiagnosticInterrupt
F1000174 | fsmFailEquipmentChassisDynamicReallocation | [FSM:FAILED]: sam:dme:EquipmentChassisDynamicReallocation | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:Chassis | sys/chassis-[id] | 1000174 | fsmFailEquipmentChassisDynamicReallocation
F1000203 | fsmFailComputePhysicalResetKvm | [FSM:FAILED]: sam:dme:ComputePhysicalResetKvm | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000203 | fsmFailComputePhysicalResetKvm
F1000209 | fsmFailMgmtControllerOnline | [FSM:FAILED]: sam:dme:MgmtControllerOnline | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | mgmt:Controller | sys/chassis-[id]/blade-[slotId]/adaptor-[id]/mgmt | 1000209 | fsmFailMgmtControllerOnline
F1000210 | fsmFailComputeRackUnitOffline | [FSM:FAILED]: sam:dme:ComputeRackUnitOffline | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:RackUnit | sys/rack-unit-[id] | 1000210 | fsmFailComputeRackUnitOffline
F1000227 | fsmFailEquipmentLocatorLedSetFiLocatorLed | [FSM:FAILED]: sam:dme:EquipmentLocatorLedSetFiLocatorLed | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:LocatorLed | sys/chassis-[id]/blade-[slotId]/locator-led | 1000227 | fsmFailEquipmentLocatorLedSetFiLocatorLed
F1000263 | fsmFailVnicProfileSetDeployAlias | [FSM:FAILED]: sam:dme:VnicProfileSetDeployAlias | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | vnic:ProfileSet | fabric/lan/profiles | 1000263 | fsmFailVnicProfileSetDeployAlias
F1000279 | fsmFailSwPhysConfPhysical | [FSM:FAILED]: sam:dme:SwPhysConfPhysical | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | sw:Phys | sys/switch-[id]/phys | 1000279 | fsmFailSwPhysConfPhysical
F1000294 | fsmFailExtvmmEpClusterRole | [FSM:FAILED]: sam:dme:ExtvmmEpClusterRole | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | extvmm:Ep | sys/extvm-mgmt | 1000294 | fsmFailExtvmmEpClusterRole
F1000302 | fsmFailEquipmentBeaconLedIlluminate | [FSM:FAILED]: sam:dme:EquipmentBeaconLedIlluminate | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | equipment:BeaconLed | sys/chassis-[id]/blade-[slotId]/beacon | 1000302 | fsmFailEquipmentBeaconLedIlluminate
F1000311 | fsmFailEtherServerIntFIoConfigSpeed | [FSM:FAILED]: sam:dme:EtherServerIntFIoConfigSpeed | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | ether:ServerIntFIo | sys/chassis-[id]/blade-[slotId]/diag/port-[portId] | 1000311 | fsmFailEtherServerIntFIoConfigSpeed
F1000321 | fsmFailComputePhysicalUpdateBIOS | [FSM:FAILED]: sam:dme:ComputePhysicalUpdateBIOS | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000321 | fsmFailComputePhysicalUpdateBIOS
F1000322 | fsmFailComputePhysicalActivateBIOS | [FSM:FAILED]: sam:dme:ComputePhysicalActivateBIOS | critical | fsm-failed | None set. | None set. | none | TRUE | fsm | compute:Physical |  | 1000322 | fsmFailComputePhysicalActivateBIOS