## Slide 1: Designing Storage Networks
Paresh Gupta (paregupt@cisco.com)
Technical Marketing Engineer
Cisco Storage Networking
for solid-state storage and next-generation virtualized applications
23-May-2017

## Slide 2: All Flash Arrays (AFA) are mainstream
Solid State Drives (SSD) has become mainstream storage media replacing Hard Disk Drives (HDD)
Top 4 factors
  Reliability
  Performance
  Scalability
  Performance consistency
Source: IDC: The Evolving All Flash Array (AFA) Market January 2017

## Slide 3: SSD vs HDD
Data stored on magnetic media
Moving mechanical parts
  Rotation motor
  Moving head
Hard Disk Drive
Solid State Drive
Data stored on electronic media
No moving mechanical parts
Higher performance
Lower power
Lower cooling requirement
Almost same cost points as of HDDs
How do you define and measure performance today?

## Slide 4: What is meant by performance?
MDS
MDS
Data Access
Latency
Exchange
Completion
Time
  Read CMD
STATUS
XFER_RDY
STATUS
MDS
MDS
Exchange
Completion
Time
  Write CMD
Data Access
Latency
  Exchange Completion time
  Data Access Latency
  Outstanding IO
  IOPS & other flow level counters
  IOPS, IO block size & other detailed flow level stats
  Failed exchanges, IO retransmissions
  SCSI error conditions (Aborts, Rejects, etc)
  Per flow timeout drop frames
To be measured at VM-SID-DID-LUN level

## Slide 5: Challenges in quantification of performance
Production deployments are getting large and complex
Production networks are much different from lab networks used for pilot testing
Limitation of tools for metric measurement
Different teams managing different components.
Teams working in silos.
Hybrid environments.
Virtualization.
Reference point of measurement matters.

## Slide 6: Understanding end-to-end block IO path
Compute & Applications
Database
Server
Web
Server
Video
Streaming
Server
OLTP
Application issues
Application
File System
Block
SCSI
FC Driver
HBA (firmware)
Too many components involved
Everybody is limited by their own view
Virtualization adds complexity
Hybrid-shared environments
    Bare-metals & virtualized servers
    Spinning disks & All flash arrays
    Multiple speed (4/8/16/32G FC)
Storage
All Flash Arrays
Spinning Disk Arrays
Drive enclosure
Backend connect
Storage Processor
FC Driver
HBA (firmware)
SAN
Writes
Reads
When application user complains, where do you start?
Not an App/host issue
Not a storage issue
Not a SAN issue

## Slide 7: Complete I/O visibility using Cisco MDS
Deep packet visibility - FC & SCSI headers
Monitor every flow, every packet, at every speed in real time
Predictive & proactive, on-wire, vendor neutral monitoring between I & T
Compute & Applications
Storage
Database
Server
Web
Server
Video
Streaming
Server
OLTP
All Flash Arrays
Spinning Disk Arrays
Application issues
Monitor the wire to find the problem
SAN
Writes
Reads
Application
File System
Block
SCSI
FC Driver
HBA (firmware)
Drive enclosure
Backend connect
Storage Processor
FC Driver
HBA (firmware)
FC
SCSI
Data

## Slide 8: Switch Native Line Rate IO visibility
Pervasive | No appliance | No probes | Always on
End to End Visibility for trouble shooting
Scale with MDS 9700 Director Platform
High Performance
Onboard analytics engine for data collection
100% Visibility
Every Packet, Every Flow, Every Speed
4/8/16/32 G Fibre Channel module for MDS 9700
Hardware is available in April 2017. Analytics functionality will be enabled in 2HCY17 by SW-only upgrade

## Slide 9: 32G FC deployment with MDS 9700 – Option 1
SAN upgrade from MDS 9500 or competition
16G or 32G FC
32G FC
4, 8, 16, 32 G FC
32G FC module
16G FC module
Full deployment using 32G FC module
Storage connectivity
16 or 32G FC
Host connectivity
4, 8, 16 or 32G FC
ISL connectivity
Up to 16 physical links at 32G FC
in a single port-channel (Up to 512 Gbps)
SAN analytics
Everywhere in the fabric. No extra device
SAN Management
Centralized using DCNM

## Slide 10: 32G FC deployment with MDS 9700 – Option 2
SAN upgrade with 16G FC on MDS 9700 – Seamless adoption of 32G FC
16G or 32G FC
16G or 32G FC
2, 4, 8, 16, 32 G FC
32G FC module
16G FC module
32G FC module for ISL or storage connectivity
Storage connectivity
16 or 32G FC using 32G FC module
Host connectivity
Use existing inventory of 16G FC module for 2/4/8/10/16G FC, 32G FC module for 32G
ISL connectivity
Use existing inventory of 16G FC module or 32G FC module for higher speed
SAN analytics
32G FC module required in data path: Either storage edge, ISLs or everywhere.
SAN Management
Centralized using DCNM

## Slide 11: Best Practice for 32G FC module on MDS 9700
Native switch-integrated fabric-wide analytics
Investment protection of 16G FC module on MDS 9700
Seamless & non-disruptive insertion of 32G FC module
High speed ISL  Increase performance with fewer links
SAN upgrade with 16G FC on MDS 9700 – Seamless adoption of 32G FC
32G FC module
16G FC module
Cisco Recommended
Possible
Existing
3
2
1

## Slide 12
Lessons learned
for SAN design with All Flash Arrays (AFA)

## Slide 13: Oversubscription in storage networks
16G
16G
16/32G
8G
AFA- 1
64K read request
Response at line rate
All Flash Arrays are extremely fast
Frames are transmitted at line rate (of the directly connected interface)
Backpressure is created if downstream links have less bandwidth
Effect is multiplied if same host makes simultaneous read requests to multiple targets almost at the same time
AFA- 2
Host-1
40µs
80µs
160µs
16G
8G
4G
Time to transmit 32 full size FC frames
Host-edge switch needs more time to transmit the frames
64K read request
Response at line rate
Increased oversubscription
Calculations are approximated to convey the message using simple numbers

## Slide 14: What changed with All Flash Arrays?
16G
16G
16/32G
8G
AFA- 1
Response at line rate
All flash arrays enable high speed random read of data from underlying media
AFA- 2
Host-1
16G
16G
16/32G
8G
Traditional
spinning-disk arrays
Response may not be at line rate
Host-1
Traditional spinning disks:
Most have 8G FC ports
Have large random-read delay (due to mechanical moving parts)
Data transmit is rarely at line rate
Larger inter-frame gap on the wire (at microsecond granularity)
All Flash Arrays
Spinning Disk Arrays

## Slide 15: Watch video for more details
https://www.youtube.com/watch?v=tY7gu16ar_Q&feature=youtu.be&list=PL1F6F23C54113557F

## Slide 16: Host Oversubscription due to speed mismatch
16G
16G
16/32G
8G
AFA- 1
AFA- 2
Host-1
Mitigation – Host IO limits on Storage Arrays (Dell EMC’s recommendation)
Limit IO per Storage Group or LUN
Limit the BW on the array to match host’s BW
Mitigates the impact in some environments, not all.
To know more if you will be benefited:
  Dell EMC VMAX3 and VMAX All Flash Quality of Service Controls for Multi-Tenant Environments
  Configuring your SAN to support All Flash Arrays – Alan Rajapa and Erik Smith - Dell EMC World 2017

## Slide 17: Design recommendation with AFA
Better
Best
16G
16G
16G
8G
AFA- 1
AFA- 2
Host-1
16G
16G
16G
16G
AFA- 1
AFA- 2
Host-1
16G
16G
32G
32G
AFA- 1
AFA- 2
Host-1
All Flash Arrays (AFA) changed everything – responses are extremely fast - FC-NVMe will make it even faster
Physical ISLs must be the highest speed links in a fabric
Host-edge should have same link speed as the storage-edge

## Slide 18: SAN Congestion
Single host does not return R_RDY
Leads to Tx B2B credit starvation on switches
Other end-devices get impacted
Explained in previous slides
16G
16G
16/32G
8G
AFA- 1
64K read request
Response at line rate
AFA- 2
Host-1
Host-edge switch needs more time to transmit the frames
64K read request
Response at line rate
Increased oversubscription
Oversubscription compared to typical slow drain due to Tx B2B credit starvation
SAN congestion due to host oversubscription
vs
SAN congestion due to Tx B2B credit starvation
Host-1
Array-1
Array-2
Host-2
R_RDY
Culprit
Impacted
Impacted
Impacted
Important – Understand the difference for effective resolution

## Slide 19: Slow Drain due to Tx B2B credit starvation
Host-1
Array-1
Array-2
Host-2
R_RDY
Culprit
Slow Drain device
Impacted
Impacted
Impacted
1
2
R_RDY
R_RDY
R_RDY
Back Pressure
Back Pressure
2
1
Fibre Channel is a loss-less fabric – achieved using B2B credits and R_RDY
A single misbehaving host, not sending back R_RDY fast enough, causes slow drain
Impact is seen on multiple end-devices sharing the same pair of switches and ISLs
Switchport connected to a slow drain device is starved for Tx B2B credits
Resolution depends on the duration of Tx B2B credit unavailability on switchport connected to the slow drain device
R_RDY

## Slide 20: SAN Congestion
16G
16G
16/32G
8G
AFA- 1
Response at line rate
AFA- 2
Host-1
Oversubscribed host link
Oversubscription compared to typical slow drain due to Tx B2B credit starvation
SAN congestion due to host oversubscription
vs
SAN congestion due to Tx B2B credit starvation
Host-1
Array-1
Array-2
Host-2
R_RDY
Culprit
Impacted
Impacted
Impacted
Host link is over-utilized No B2B credit starvation | Host link is under-utilized B2B credit starvation
ISL utilization is limited by host BW B2B credit starvation | ISL is under-utilized B2B credit starvation
Use TxWait and tx-datarate counters under port-monitor feature on Cisco MDS to find the difference

## Slide 21: Virtual Link (VL) isolation of slow drain device
Host-1
Array-1
Array-2
Host-2
R_RDY
Culprit
Slow Drain device
Impacted
Impacted
Impacted
1
R_RDY
R_RDY
R_RDY
Back Pressure
Back Pressure
1
Slow Drain device is moved to Isolated state
All traffic destined to isolated port is moved to low priority Virtual Link
All virtual links have dedicated B2B credits
B2B credit starvation in low priority virtual link does not impact B2B credits in normal priority virtual link
Low Priority VL
Normal Priority VL
R_RDY
R_RDY
Back Pressure
Released
Back Pressure
Released
Moved to Isolated state
2

## Slide 22
Investment Protection for the Next Decade
NVMe-over Fabric: Improved Performance and Faster Response

## Slide 23: What is NVMe?
  Written from ground-up (Incorporated years of learnings and best practices)
  Up to 64K queues for command submission and completion, each CPU core can have its own queues
  Streamlined and simple command sets and many more…
Non-Volatile Memory based storage (flash or solid state) has been widely adopted
There are no more rotating motors or moving heads in the storage drives
Reads and Writes are extremely fast
Storage
CPU are extremely fast, multi-core, hyper-threaded
Compute
Interconnect between CPU and storage is very fast (PCI 3.0 or > 100 Gbps fabrics)
Network
The traditional SW layer (SATA or SAS) unable to take full advantage
Software
Welcome NVMe

## Slide 24: NVMe over FC – Same FC Paradigm
HBA
HBA
Traditional FC-SCSI capable initiator
FC-NVMe capable initiator
Traditional FC-SCSI capable target
FC-NVMe capable target
FC or FCoE fabric built using
Cisco MDS 9000 switches
Cisco C-series Rack Servers
Increased Performance
Ecosystem Support
Phased Transition
Seamless Insertion
Multiprotocol Flexibility
No New Network
Established Solution
Co-exists with current Solutions
Notes: Increased Performance: Unleash the power of All flash arrays using NVMe over FC or FCoE
Seamless Insertion: Support on all existing 16G FC and new 32G FC MDS switches
Phased Transition: SCSI & NVMe initiators & targets continue to share same SAN
Multiprotocol flexibility: SCSI or NVMe traffic over FC or FCoE transport
Ecosystem support: Fully validated solution on UCS C-series servers, MDS switches, Broadcom & Avago HBAs

## Slide 25: Fibre Channel Architecture & NVMe
FC-4
FC-2
FC-1
FC-0
Application
SCSI
ESCON
IP
Framing & Flow Control
Encoding
IP
NVMe
FC-3
Generic Services
Physical Interface (1-32G FC)
ULP
Mapping
FC-NVMe extends benefits of NVMe over Fibre Channel fabric
Utilize FC benefits like plug-n-play, fabric server, name server, zone server, etc.
Deploy in existing infrastructure using current HBAs, switches, and management software
FC-NVMe, SCSI-FCIP and FICON can be transported concurrently in the same fabric

## Slide 26: FC-NVMe – Phased & Seamless transition
FC-NVMe end-devices are dual-stack – simultaneous support of NVMe and SCSI transport
Cisco MDS enable simultaneous switching of NVMe & SCSI transport encapsulated in Fibre Channel frames
SCSI-only or NVMe capability of end-devices is auto-detected and advertised
Similar to the existing plug-and-play architecture of Fibre Channel
FC-NVMe is independent of FC speed. Possible even at 2G FC. 32G FC recommended.
Traditional FC-SCSI capable initiator
FC-NVMe capable initiator
Traditional FC-SCSI capable target
FC-NVMe capable target
FC
SCSI
FC
SCSI
NVMe
HBA
HBA
FC
SCSI
FC
SCSI
NVMe
Cisco C-series Rack Servers
Cisco MDS

## Slide 27: FC-NVMe – Phased & Seamless transition
MDS9700# show fcns database vsan 160
VSAN 160:
--------------------------------------------------------------------------
FCID TYPE PWWN (VENDOR) FC4-TYPE:FEATURE
--------------------------------------------------------------------------
0x590020 N 10:00:00:90:fa:e0:08:5d (Emulex) scsi-fcp:init NVMe:init
0x590140 N 21:00:00:24:ff:7f:06:39 (Qlogic) scsi-fcp:init NVMe:init
(showing entries only for dual-stack NVMe capable initiators. Other devices will look similar)
FCNS database
Traditional FC-SCSI capable initiator
FC-NVMe capable initiator
Traditional FC-SCSI capable target
FC-NVMe capable target
FC
SCSI
FC
SCSI
NVMe
HBA
HBA
FC
SCSI
FC
SCSI
NVMe
Cisco C-series Rack Servers
Cisco MDS
I am a
SCSI initiator
I am a
SCSI & NVMe initiator
I am a
SCSI target
I am a
SCSI & NVMe target
Fibre Channel Name Server (FCNS) is a distributed database on MDS switches
End-devices register Upper Layer Protocol (ULP) with FCNS database, to be advertised to other end-devices in the same zone

## Slide 28: FC-NVMe – Interop certified by Cisco
FC-NVMe capable target
HBA
Cisco C-series Rack Servers
Cisco MDS 9000
(All 16G and 32G switches)
HBA
Broadcom / Emulex
Cavium / Qlogic

## Slide 29
Key Takeaways

## Slide 30: Key Takeaways
Industry’s first and only line-rate, integrated SAN analytics solution
Proactive & Predictive problem resolution
Enabling technology transition
NVMe over FC : Scale Flash deployments
Seamless transition
Low Cost, Low Risk, Low turnaround
Deep Visibility
Investment Protection
High speed connectivity
Physical ISL must be the highest speed links in a fabric
Host-edge should have same link speed as the storage-edge
Use of VSANs or Virtual Links
SAN Design for AFA